## Sheet1
Sl. | Room name | Room no. | Equipment | Quantity | LOAD Per Quantity (W) | Total Load ( KW) | voltage | Current (A) | Apparent (KVA | phase | power factor | Total Load (Per Room_KW) | Load Type (Continous/Discont.) | Total Load (Building_kW)
1 | Foyer | Room 100 | [9 empty] | 4.8445
| Foyer | Room 100 | Receptacles (2-15A) | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95
| Foyer | Room 100 | Light | 1 | 40 | 0.04 | 24 | 1.7544 | 0.042105 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | Close Circuit Camera | 2 | 5.5 | 0.011 | 12 | 0.96491 | 0.011579 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | Barrier free access | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | Push switch | 2 | 1 | 0.002 | 24 | 0.087719 | 0.0021053 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | 120V 6FLA FF-1 | 1 | 720 | 0.72 | 120 | 6.3158 | 0.75789 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | Annunciator Panel used as Fire fighter access point | 1 | 400 | 0.4 | 120 | 3.5088 | 0.42105 | 1 | 0.95 |  | Continous
2 | Classroom | Room 101 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 8.467 | Discontinous
| Classroom | Room 101 | Receptacles (4-15A) | 4 | 1800 | 7.2 | 120 | 63.1579 | 7.5789 | 1 | 0.95 |  | Discontinous
| Classroom | Room 101 | Light | 9 | 40 | 0.36 | 120 | 3.1579 | 0.37895 | 1 | 0.95 |  | Continous
| Classroom | Room 101 | Projector | 1 | 400 | 0.4 | 120 | 3.5088 | 0.42105 | 1 | 0.95 |  | Discontinous
| Classroom | Room 101 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Classroom | Room 101 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Classroom | Room 101 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
| Classroom | Room 101 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Classroom | Room 101 | Computer | 1 | 260 | 0.26 | 120 | 2.2807 | 0.27368 | 1 | 0.95 |  | Discontinous
| Classroom | Room 101 | Speaker | 1 | 220 | 0.22 | 120 | 1.9298 | 0.23158 | 1 | 0.95 |  | Discontinous
3 | Closet | Room 102 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 3.624 | Discontinous
| Closet | Room 102 | Receptacles | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95 |  | Discontinous
| Closet | Room 102 | Light | 4 | 6 | 0.024 | 120 | 0.21053 | 0.025263 | 1 | 0.95 |  | Continous
4 | W. Washrrom | Room 103 | [5 empty] | #DIV/0! | 0 | 1 | 0.95 | 7.2605 | Discontinous
| W. Washrrom | Room 103 | Receptacles waterproof (3-15A) | 3 | 1800 | 5.4 | 120 | 47.3684 | 5.6842 | 1 | 0.95 |  | Discontinous
| W. Washrrom | Room 103 | Light / Sensor light | 16 | 12 | 0.192 | 120 | 1.6842 | 0.20211 | 1 | 0.95 |  | Continous
| W. Washrrom | Room 103 | Hand Dryer Automatic | 1 | 1600 | 1.6 | 120 | 14.0351 | 1.6842 | 1 | 0.95 |  | Discontinous
| W. Washrrom | Room 103 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| W. Washrrom | Room 103 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| W. Washrrom | Room 103 | Barrier free Access | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| W. Washrrom | Room 103 | Push Switch | 2 | 1 | 0.002 | 24 | 0.087719 | 0.0021053 | 1 | 0.95 |  | Continous
5 | M. Washroom | Room 104 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 3.0725 | Discontinous | 250.6398
| M. Washroom | Room 104 | Receptacles waterproof (1-15A) | 1 | 1800 | 1.8 | 120 | 15.7895 | 1.8947 | 1 | 0.95 |  | Discontinous
| M. Washroom | Room 104 | Light / Sensor light | 7 | 12 | 0.084 | 120 | 0.73684 | 0.088421 | 1 | 0.95 |  | Continous
| M. Washroom | Room 104 | Hand Dryer Automatic | 1 | 120 | 0.12 | 120 | 1.0526 | 0.12632 | 1 | 0.95 |  | Discontinous
| M. Washroom | Room 104 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| M. Washroom | Room 104 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| M. Washroom | Room 104 | Barrier free Access | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| M. Washroom | Room 104 | Push Switch | 2 | 1 | 0.002 | 24 | 0.087719 | 0.0021053 | 1 | 0.95 |  | Continous
| M. Washroom | Room 104 | BBH-8 120V 1phase, 1KW | 1 | 1000 | 1 | 120 | 8.7719 | 1.0526 | 1 | 0.95 |  | Continous
6 | Washroom Corridor | Room 105 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 0.0275 | Discontinous
| Washroom Corridor | Room 105 | Light | 2 | 3 | 0.006 | 120 | 0.052632 | 0.0063158 | 1 | 0.95 |  | Continous
| Washroom Corridor | Room 105 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Washroom Corridor | Room 105 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Washroom Corridor | Room 105 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
7 | Janitor | Room 106 | Receptacles (1-20A) | 1 | 1800 | 1.8 | 120 | 15.7895 | 1.8947 | 1 | 0.95 | 1.818 | Discontinous
| Janitor | Room 106 | Light | 2 | 9 | 0.018 | 120 | 0.15789 | 0.018947 | 1 | 0.95 |  | Continous
8 | Water Meter | Room 107 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 0.75 | Discontinous
| Water Meter | Room 107 | Light | 1 | 10 | 0.01 | 120 | 0.087719 | 0.010526 | 1 | 0.95 |  | Continous
| Water Meter | Room 107 | Sprinkler Flow Switch and Temper Switch1 | 1 | 20 | 0.02 | 120 | 0.17544 | 0.021053 | 1 | 0.95 |  | Discontinous
| Water Meter | Room 107 | FF-4 120V 1phase 6FLA | 1 | 720 | 0.72 | 120 | 6.3158 | 0.75789 | 1 | 0.95 |  | Continous
9 | Catering Kicthenette | Room 108 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 22.3478 | Discontinous
| Catering Kicthenette | Room 108 | Receptacles Waterproof (4-20A/ 1-30A/1-15A) | 6 | 1800 | 10.8 | 120 | 94.7368 | 11.3684 | 1 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Light | 13 | 40 | 0.52 | 120 | 4.5614 | 0.54737 | 1 | 0.95 |  | Continous
| Catering Kicthenette | Room 108 | Fridge | 1 | 725 | 0.725 | 120 | 6.3596 | 0.76316 | 1 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Dishwasher | 1 | 1300 | 1.3 | 120 | 11.4035 | 1.3684 | 1 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Espresso Machines | 1 | 1500 | 1.5 | 120 | 13.1579 | 1.5789 | 1 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Digital Display | 1 | 110 | 0.11 | 120 | 0.96491 | 0.11579 | 1 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Flat top grill | 1 | 2700 | 2.7 | 208 | 13.664 | 2.8421 | 3 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Water Purifier | 1 | 60 | 0.06 | 120 | 0.52632 | 0.063158 | 1 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Commercial Oven | 1 | 1100 | 1.1 | 208 | 5.5668 | 1.1579 | 3 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Catering Kicthenette | Room 108 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Catering Kicthenette | Room 108 | Close Circuit Camera | 2 | 5.5 | 0.011 | 12 | 0.96491 | 0.011579 | 1 | 0.95 |  | Continous
| Catering Kicthenette | Room 108 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Catering Kicthenette | Room 108 | Exhaust Fan | 1 | 0.25 | 0.00025 | 120 | 0.002193 | 0.00026316 | 1 | 0.95 |  | Continous
| Catering Kicthenette | Room 108 | BBH-1 | 1 | 2500 | 2.5 | 208 | 12.6518 | 2.6316 | 1 | 0.95 |  | Continous
| Catering Kicthenette | Room 108 | BBH-2 | 1 | 1000 | 1 | 120 | 8.7719 | 1.0526 | 1 | 0.95 |  | Continous
10 | Commons | Room 109 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 12.2775 | Discontinous
| Commons | Room 109 | Receptacles ( 3-15A) | 3 | 1800 | 5.4 | 120 | 47.3684 | 5.6842 | 1 | 0.95 |  | Discontinous
| Commons | Room 109 | Light | 12 | 36 | 0.432 | 120 | 3.7895 | 0.45474 | 1 | 0.95 |  | Continous
| Commons | Room 109 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Commons | Room 109 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Commons | Room 109 | Close Circuit Camera | 4 | 5.5 | 0.022 | 12 | 1.9298 | 0.023158 | 1 | 0.95 |  | Continous
| Commons | Room 109 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Commons | Room 109 | Projector | 2 | 400 | 0.8 | 120 | 7.0175 | 0.84211 | 1 | 0.95 |  | Discontinous
| Commons | Room 109 | Barrier free access | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| Commons | Room 109 | Push button | 2 | 1 | 0.002 | 24 | 0.087719 | 0.0021053 | 1 | 0.95 |  | Continous
| Commons | Room 109 | Egress Door | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| Commons | Room 109 | BBH-3 120 V | 1 | 1000 | 1 | 120 | 8.7719 | 1.0526 | 1 | 0.95 |  | Continous
| Commons | Room 109 | BBH-4 208 V | 1 | 2500 | 2.5 | 208 | 12.6518 | 2.6316 | 1 | 0.95 |  | Continous
| Commons | Room 109 | BBH-5 120 V | 1 | 1000 | 1 | 120 | 8.7719 | 1.0526 | 1 | 0.95 |  | Continous
| Commons | Room 109 | BBH-9 120V | 1 | 1000 | 1 | 120 | 8.7719 | 1.0526 | 1 | 0.95 |  | Continous
11 | Cultural Room | Room 110 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 53.4695 | Discontinous
| Cultural Room | Room 110 | Receptacles (5-15A) | 5 | 1800 | 9 | 120 | 78.9474 | 9.4737 | 1 | 0.95 |  | Discontinous
| Cultural Room | Room 110 | Light Proper for spotting | 11 | 150 | 1.65 | 120 | 14.4737 | 1.7368 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Close Circuit Camera | 4 | 5.5 | 0.022 | 12 | 1.9298 | 0.023158 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Projector | 2 | 400 | 0.8 | 120 | 7.0175 | 0.84211 | 1 | 0.95 |  | Discontinous
| Cultural Room | Room 110 | Barrier free access | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Push button | 1 | 1 | 0.001 | 24 | 0.04386 | 0.0010526 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Egress Door | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Microphone | 2 | 2 | 0.004 | 12 | 0.35088 | 0.0042105 | 1 | 0.95 |  | Discontinous
| Cultural Room | Room 110 | Speaker | 1 | 220 | 0.22 | 120 | 1.9298 | 0.23158 | 1 | 0.95 |  | Discontinous
| Cultural Room | Room 110 | BBH-6 1phase 2.5 KW 208 V | 1 | 2500 | 2.5 | 208 | 12.6518 | 2.6316 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | BBH-7 1phase 2.5 KW 208 V | 1 | 2500 | 2.5 | 208 | 12.6518 | 2.6316 | 1 | 0.95 |  | Continous
| Exterior Sub of Culture | Room 110 | Condensing unit,208,3ph,14fla | 1 | 4791 | 4.791 | 208 | 24.246 | 5.0432 | 3 | 0.95 |  | Continous
| Exterior Sub of Culture | Room 110 | Condensing unit,208,3ph,18fla | 1 | 6160 | 6.16 | 208 | 31.1741 | 6.4842 | 3 | 0.95 |  | Continous
| Exterior Sub of Culture | Room 110 | Condensing unit,208,3ph,39fla | 1 | 13000 | 13 | 208 | 65.7895 | 13.6842 | 3 | 0.95 |  | Continous
| Exterior Sub of Culture | Room 110 | Condensing unit,208,3ph,37fla | 1 | 12700 | 12.7 | 208 | 64.2713 | 13.3684 | 3 | 0.95 |  | Continous
12 | Storage | Room 111 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 3.624 | Discontinous
| Storage | Room 111 | Receptacles (2-15A) | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95 |  | Discontinous
| Storage | Room 111 | Light | 1 | 24 | 0.024 | 120 | 0.21053 | 0.025263 | 1 | 0.95 |  | Continous
13 | Snack | Room 112 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 11.556 | Discontinous
| Snack | Room 112 | Receptacles (1-15A/ 3-20A) | 4 | 1800 | 7.2 | 120 | 63.1579 | 7.5789 | 1 | 0.95 |  | Discontinous
| Snack | Room 112 | Light | 3 | 48 | 0.144 | 120 | 1.2632 | 0.15158 | 1 | 0.95 |  | Continous
| Snack | Room 112 | Microwave | 1 | 1000 | 1 | 120 | 8.7719 | 1.0526 | 1 | 0.95 |  | Discontinous
| Snack | Room 112 | Coffee Machine | 1 | 1460 | 1.46 | 120 | 12.807 | 1.5368 | 1 | 0.95 |  | Discontinous
| Snack | Room 112 | Fridge | 1 | 725 | 0.725 | 120 | 6.3596 | 0.76316 | 1 | 0.95 |  | Discontinous
| Snack | Room 112 | Warming Oven | 1 | 1000 | 1 | 120 | 8.7719 | 1.0526 | 1 | 0.95 |  | Discontinous
| Snack | Room 112 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Snack | Room 112 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Snack | Room 112 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
| Snack | Room 112 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
14 | Information | Room 113 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 5.9235 | Discontinous
| Information | Room 113 | Receptacles ( 3-15A) | 3 | 1800 | 5.4 | 120 | 47.3684 | 5.6842 | 1 | 0.95 |  | Discontinous
| Information | Room 113 | Light | 6 | 40 | 0.24 | 120 | 2.1053 | 0.25263 | 1 | 0.95 |  | Continous
| Information | Room 113 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Information | Room 113 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Information | Room 113 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
| Information | Room 113 | Computer | 1 | 260 | 0.26 | 120 | 2.2807 | 0.27368 | 1 | 0.95 |  | Discontinous
15 | Room 114 | Room 114 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 3.615 | Discontinous
| Room 114 | Room 114 | Receptacles (2-15A) | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95 |  | Discontinous
| Room 114 | Room 114 | Light | 3 | 5 | 0.015 | 120 | 0.13158 | 0.015789 | 1 | 0.95 |  | Continous
16 | Yukuta | Room 115 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 1.91 | Discontinous
| Yukuta | Room 115 | Receptacles (1-15A) | 1 | 1800 | 1.8 | 120 | 15.7895 | 1.8947 | 1 | 0.95 |  | Discontinous
| Yukuta | Room 115 | Light | 6 | 10 | 0.06 | 120 | 0.52632 | 0.063158 | 1 | 0.95 |  | Continous
| Yukuta | Room 115 | Climate Controlled | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
17 | Education | Room 116 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 8.447 | Discontinous
| Education | Room 116 | Receptacles (3-15A/ 1-15A) | 4 | 1800 | 7.2 | 120 | 63.1579 | 7.5789 | 1 | 0.95 |  | Discontinous
| Education | Room 116 | Light | 5 | 40 | 0.2 | 120 | 1.7544 | 0.21053 | 1 | 0.95 |  | Continous
| Education | Room 116 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Education | Room 116 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Education | Room 116 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
| Education | Room 116 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Education | Room 116 | Computer | 2 | 260 | 0.52 | 120 | 4.5614 | 0.54737 | 1 | 0.95 |  | Discontinous
| Education | Room 116 | Printer, Scanner, Copier | 1 | 500 | 0.5 | 120 | 4.386 | 0.52632 | 1 | 0.95 |  | Discontinous
18 | Mechanical | Room 117 |  |  |  | 0 |  | #DIV/0! | #DIV/0! |  |  | 8.624 | Discontinous
| Mechanical | Room 117 | Receptacles (1-20A/1-15A) | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95 |  | Discontinous
| Mechanical | Room 117 | Light | 6 | 10 | 0.06 | 120 | 0.52632 | 0.063158 | 1 | 0.95 |  | Continous
| Mechanical | Room 117 | Access Control | 1 | 20 | 0.02 | 120 | 0.17544 | 0.021053 | 1 | 0.95 |  | Continous
| Mechanical | Room 117 | force flow fan,120V,1ph,1.5KW FF3 | 1 | 1500 | 1.5 | 120 | 13.1579 | 1.5789 | 1 | 0.95 |  | Continous
| Mechanical | Room 117 | furnace,208,3ph,10fla F-1, F-2(2) | 1 | 3422.5 | 3.4225 | 208 | 17.3203 | 3.6026 | 3 | 0.95 |  | Continous
| Mechanical | Room 117 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Mechanical | Room 117 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Mechanical | Room 117 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
19 | Staff | Room 118 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 5.4985 | Discontinous
| Staff | Room 118 | Receptacles (3-15A) | 3 | 1800 | 5.4 | 120 | 47.3684 | 5.6842 | 1 | 0.95 |  | Discontinous
| Staff | Room 118 | Light | 4 | 20 | 0.08 | 120 | 0.70175 | 0.084211 | 1 | 0.95 |  | Continous
| Staff | Room 118 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Staff | Room 118 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
20 | Administration | Room 119 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 6.647 | Discontinous
| Administration | Room 119 | Receptacles (1-20A/2-15A) | 3 | 1800 | 5.4 | 120 | 47.3684 | 5.6842 | 1 | 0.95 |  | Discontinous
| Administration | Room 119 | Light | 5 | 40 | 0.2 | 120 | 1.7544 | 0.21053 | 1 | 0.95 |  | Continous
| Administration | Room 119 | Computer | 2 | 260 | 0.52 | 120 | 4.5614 | 0.54737 | 1 | 0.95 |  | Discontinous
| Administration | Room 119 | Printer, Scanner, Copier | 1 | 500 | 0.5 | 120 | 4.386 | 0.52632 | 1 | 0.95 |  | Discontinous
| Administration | Room 119 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Administration | Room 119 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Administration | Room 119 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
| Administration | Room 119 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
21 | Vestibule | Room 120 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 6.317 | Discontinous
| Vestibule | Room 120 | Receptacles (2-15A) | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95 |  | Discontinous
| Vestibule | Room 120 | Light | 5 | 10 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| Vestibule | Room 120 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Vestibule | Room 120 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Vestibule | Room 120 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
| Vestibule | Room 120 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Vestibule | Room 120 | Access Control | 1 | 20 | 0.02 | 120 | 0.17544 | 0.021053 | 1 | 0.95 |  | Continous
| Vestibule | Room 120 | exhaust fan,208,3ph,1.5HP | 1 | 1120 | 1.12 | 208 | 5.668 | 1.1789 | 3 | 0.95 |  | Continous
| Vestibule | Room 120 | force flow fan,120V,1ph, 1.5KW FF-2 | 1 | 1500 | 1.5 | 120 | 13.1579 | 1.5789 | 1 | 0.95 |  | Continous
22 | Classroom | Room 121 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 9.0525 | Discontinous
| Classroom | Room 121 | Receptacles (4-15A) | 4 | 1800 | 7.2 | 120 | 63.1579 | 7.5789 | 1 | 0.95 |  | Discontinous
| Classroom | Room 121 | Light | 9 | 40 | 0.36 | 120 | 3.1579 | 0.37895 | 1 | 0.95 |  | Continous
| Classroom | Room 121 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Classroom | Room 121 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Classroom | Room 121 | Close Circuit Camera | 2 | 5.5 | 0.011 | 12 | 0.96491 | 0.011579 | 1 | 0.95 |  | Continous
| Classroom | Room 121 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Classroom | Room 121 | Computer | 1 | 260 | 0.26 | 120 | 2.2807 | 0.27368 | 1 | 0.95 |  | Discontinous
| Classroom | Room 121 | Projector | 1 | 400 | 0.4 | 120 | 3.5088 | 0.42105 | 1 | 0.95 |  | Discontinous
| Classroom | Room 121 | Sound System | 1 | 800 | 0.8 | 120 | 7.0175 | 0.84211 | 1 | 0.95 |  | Discontinous
23 | Exhibit | Room 122 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 6.9525 | Discontinous
| Exhibit | Room 122 | Receptacles (3-15A) | 3 | 1800 | 5.4 | 120 | 47.3684 | 5.6842 | 1 | 0.95 |  | Discontinous
| Exhibit | Room 122 | Light | 10 | 20 | 0.2 | 120 | 1.7544 | 0.21053 | 1 | 0.95 |  | Continous
| Exhibit | Room 122 | Spot Light | 6 | 20 | 0.12 | 120 | 1.0526 | 0.12632 | 1 | 0.95 |  | Continous
| Exhibit | Room 122 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Exhibit | Room 122 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Exhibit | Room 122 | Close Circuit Camera | 2 | 5.5 | 0.011 | 12 | 0.96491 | 0.011579 | 1 | 0.95 |  | Continous
| Exhibit | Room 122 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Exhibit | Room 122 | Projector | 1 | 400 | 0.4 | 120 | 3.5088 | 0.42105 | 1 | 0.95 |  | Discontinous
| Exhibit | Room 122 | Sound System | 1 | 800 | 0.8 | 120 | 7.0175 | 0.84211 | 1 | 0.95 |  | Discontinous
24 | Tea | Room 123 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 1.9675 | Discontinous
| Tea | Room 123 | Receptacles (1-15A) | 1 | 1800 | 1.8 | 120 | 15.7895 | 1.8947 | 1 | 0.95 |  | Discontinous
| Tea | Room 123 | Light Minimal | 4 | 36 | 0.144 | 120 | 1.2632 | 0.15158 | 1 | 0.95 |  | Continous
| Tea | Room 123 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Tea | Room 123 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Tea | Room 123 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
25 | Stairwell | Room 200 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 0.0635 | Discontinous
| Stairwell | Room 200 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 |  | Discontinous
| Stairwell | Room 200 | Light | 2 | 10 | 0.02 | 120 | 0.17544 | 0.021053 | 1 | 0.95 |  | Continous
| Stairwell | Room 200 | Access Control | 1 | 20 | 0.02 | 120 | 0.17544 | 0.021053 | 1 | 0.95 |  | Continous
| Stairwell | Room 200 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Stairwell | Room 200 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Stairwell | Room 200 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
26 | Electrical | Room 202 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 29.0575 | Discontinous
| Electrical | Room 202 | Receptacles (2-15A) | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95 |  | Discontinous
| Electrical | Room 202 | Light | 27 | 55 | 1.485 | 120 | 13.0263 | 1.5632 | 1 | 0.95 |  | Continous
| Electrical | Room 202 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Electrical | Room 202 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Electrical | Room 202 | Close Circuit Camera | 2 | 5.5 | 0.011 | 12 | 0.96491 | 0.011579 | 1 | 0.95 |  | Continous
| Electrical | Room 202 | Fire Alarm Control Panel | 1 | 960 | 0.96 | 120 | 8.4211 | 1.0105 | 1 | 0.95 |  | Continous
| Electrical | Room 202 | Fire Pump (30 HP) | 1 | 22380 | 22.38 | 208 | 113.2591 | 23.5579 | 3 | 0.95 |  | Continous
| Electrical | Room 202 | Fire Alarm Booster panel | 1 | 600 | 0.6 | 120 | 5.2632 | 0.63158 | 1 | 0.95 |  | Continous
| Electrical | Room 202 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
27 | Mechanical | Room 203 |  |  |  | 0 |  | #DIV/0! | #DIV/0! |  |  | 16.006 | Discontinous
| Mechanical | Room 203 | Receptacles (2-15A) | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95 |  | Discontinous
| Mechanical | Room 203 | Light | 13 | 65 | 0.845 | 120 | 7.4123 | 0.88947 | 1 | 0.95 |  | Continous
| Mechanical | Room 203 | Exhaust Fan,120,1ph,0.25HP | 1 | 187 | 0.187 | 120 | 1.6404 | 0.19684 | 1 | 0.95 |  | Continous
| Mechanical | Room 203 | Furnace,208,3ph,10FLA | 1 | 3422.5 | 3.4225 | 208 | 17.3203 | 3.6026 | 3 | 0.95 |  | Continous
| Mechanical | Room 203 | Furnace,208,3ph,12FLA | 1 | 3422.5 | 3.4225 | 208 | 17.3203 | 3.6026 | 3 | 0.95 |  | Continous
| Mechanical | Room 203 | Domestic hot water tank,120V,1ph 5FLA | 1 | 4500 | 4.5 | 240 | 19.7368 | 4.7368 | 1 | 0.95 |  | Continous
| Mechanical | Room 203 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Mechanical | Room 203 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Mechanical | Room 203 | Close Circuit Camera | 2 | 5.5 | 0.011 | 12 | 0.96491 | 0.011579 | 1 | 0.95 |  | Continous
28 | Telecom | Room 204 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 7.4195 | Discontinous
| Telecom | Room 204 | Receptacles (3-15A) | 3 | 1800 | 5.4 | 120 | 47.3684 | 5.6842 | 1 | 0.95 |  | Discontinous
| Telecom | Room 204 | Light | 31 | 56 | 1.736 | 120 | 15.2281 | 1.8274 | 1 | 0.95 |  | Continous
| Telecom | Room 204 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Telecom | Room 204 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Telecom | Room 204 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
| Telecom | Room 204 | Computer | 1 | 260 | 0.26 | 120 | 2.2807 | 0.27368 | 1 | 0.95 |  | Discontinous

## Sheet2
Equipment
Receptacles
Light
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Barrier free access
Fire Fighter Accesspoint
Emergency light and exit sign
Push switch
120V 6FLA FF-1
Receptacles
Light
Projector
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Emergency light and exit sign
Computer
Receptacles
Light
Receptacles waterproof
Light / Sensor light
Hand Dryer Automatic
Wifi
Intercom
Fire Alarm System
Sprinkler
Smoke Detector
Emergency light and exit sign
Barrier free Access
Push Switch
Receptacles waterproof
Light / Sensor light
Hand Dryer Automatic
Wifi
Intercom
Fire Alarm System
Sprinkler
Smoke Detector
Emergency light and exit sign
Barrier free Access
Push Switch
BBH-8 120V 1phase, 1KW
Receptacles
Light
Wifi
Intercom
Fire Alarm System
Sprinkler
Smoke Detector
Emergency light and exit sign
Light
Receptacles
Light
FF-4 120V 1phase 6FLA
Receptacles Waterproof
Light
Fridge
Dishwasher
Espresso Machines
Digital Display
Flat top grill
Water Purifier
Commercial Oven
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Emergency light and exit sign
Exhaust Fan
Bus Bar Hub 120V, 1KW BBH-1
Bus Bar Hub 208V, 2.5 KW BBH-2
Receptacles
Light
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Emergency light and exit sign
Projector
Barrier free access
Push button
Egress Door
Emergency Door
BBH-3 120 V
BBH-4 208 V
BBH-5 120 V
BBH-9 120V
Receptacles
Light Proper for spotting
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Emergency light and exit sign
Projector
Barrier free access
Push button
Egress Door
Microphone
Speaker
Emergency Exit door
BBH-6 1phase 2.5 KW 208 V
BBH-7 1phase 2.5 KW 208 V
Condensing unit,208,3ph,14fla
Condensing unit,208,3ph,18fla
Condensing unit,208,3ph,39fla
Condensing unit,208,3ph,37fla
Receptacles
Light
Receptacles
Light
Microwave
Coffee Machine
Fridge
Warming Oven
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Emergency light and exit sign
Receptacles
Light
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Computer
Receptacles
Light
Receptacles
Light
Climate Controlled
Receptacles
Light
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Emergency light and exit sign
Computer
Printer, Scanner, Copier
Receptacles
Light
Access Control Sysem
force flow fan,120V,1ph,1.5KW FF3
furnace,208,3ph,10fla F-1, F-2(2)
Wifi
Intercom
Fire Alarm System
Sprinkler
Smoke Detector
Emergency light and exit sign
Receptacles
Light
Wifi
CCTV
Receptacles
Light
Computer
Printer, Scanner, Copier
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Emergency light and exit sign
Receptacles
Light
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Emergency light and exit sign
Access Control
exhaust fan,208,3ph,1.5HP
force flow fan,120V,1ph, 1.5KW FF-2
Receptacles
Light
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Emergency light and exit sign
Computer
Projector
Sound System
Receptacles
Light
Spot Light
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Emergency light and exit sign
Projector
Sound System
Receptacles
Light Minimal
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Receptacles
Light
Access Control
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Receptacles
Light
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Emergency light and exit sign
Receptacles (1-20A)
Light
Exhaust Fan,120,1ph,0.25HP
Furnace,208,3ph,10FLA
Furnace,208,3ph,12FLA
Domestic hot water tank,120V,1ph 5FLA
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Receptacles
Light
Wifi
Intercom
CCTV
Fire Alarm System
Sprinkler
Smoke Detector
Computer