## Panel scheduiling
Room Name | Room 100 Foyer | Room 101 Classroom | Room 102 Closet | Room 103 W. Washrrom | Room 104 M. Washroom | Room 105 Washroom Corridor | Room 106 Janitor | Room 200 Stairwell | Room 107 Water Meter | Room 108 Catering Kicthenette | Room 110 Cultural Room | Room 109 Commons | Room 111 Storage | Room 112 Snack | Room 113 Information | Room 114 Storage | Room 115 Yukuta | Room 116 Education | Room 118 Staff | Room 119 Administration | Room 117 Mechanical | Room 120 Vestibule | Room 121 Classroom | Room 122 Exhibit | Room 123 Tea | Room 202 Electrical | Room 203 Mechanical | Room 204 Telecom
Load (KW) | 4.84 | 8.46 | 3.624 | 7.26 | 3.07 | 0.0275 | 1.81 | 0.063 | 0.75 | 22.34 | 53.46 | 12.27 | 5.42 | 11.55 | 5.92 | 3.61 | 1.91 | 8.44 | 5.49 | 6.64 | 8.64 | 6.317 | 9.05 | 6.95 | 1.96 | 29.05 | 16 | 7.41
Panel | 12A | [8 empty] | 12B | 12C | 12D |  |  | 12E | [5 empty] | 12F | 12G |  |  |  | M2H
Current (A) /Room | 24.5411 | 42.8963 | 18.3754 | 36.8117 | 15.5664 | 0.13944 | 9.1776 | 0.31944 | 3.8029 |  |  | 62.2148 | 27.482 | 58.564 | 30.0172 | 18.3044 | 9.6846 | 42.7948 | 27.8369 | 33.668 |  | 32.0302 | 45.8878 | 35.2398 | 9.9381 | 147.2974 | 81.1277 | 37.5723
Switch Size/Room
Total KW | 29.9045 | [8 empty] | 22.34 | 53.46 | 29.24 |  |  | 32.01 | [5 empty] | 8.64 |  | 24.277 |  |  |  | 52.46
Current (A) | 151.6302 | [8 empty] | 113.2745 | 271.0678 | 148.2608 |  |  | 162.3061 | [5 empty] | 43.8089 |  | 123.096 |  |  |  | 265.9974
MCCB (A) | 189.5377 | [8 empty] | 141.5931 | 338.8348 | 185.326 |  |  | 202.8826 | [5 empty] | 54.7612 |  | 153.87 |  |  |  | 332.4967
Disconnected Switch (A) | [9 empty] | 141.5931 | 338.8348 | [9 empty] | 54.7612

## 12A
Panel Schedule
Date |  |  |  | Panel ID | 12A |  |  |  |  | Breaker (A) |  | Main Breaker/MLO
Project Name |  |  |  | Mountaining Type | Surface |  |  |  |  | Total Circuit |  | ISC Rating
Location |  |  |  | Voltage (V) | 120/208 |  |  |  |  | BUS Rating (A) |  | ISCA (Calculated)
Owner Details |  |  |  | Phase | 3 |  |  |  |  | No. Wire | 4
Note
Room No | Circuit No | Equipments Description | Quantity | Load (KVA) | Pole | Breaker Size | BUS | Breaker Size | Pole | Load (KVA) | Quantity | Equipments Description | Circuit No | Room No
101-107, 200 | 1 | Receptacles (15A) | 1 | 1.85 | 1 | 20 | A | 40 | 1 | 3.7895 | 2 | Receptacles (20A) | 2 | 101-107, 200
| 3 | Receptacles (15A) | 2 | 3.7 | 1 | 39 | B | 1 | 1 | 0.021053 | 1 | Sprinkler Flow Switch and Temper Switch1 | 4
| 5 | Receptacles (15A) | 5 | 9.25 | 1 | 97 | C | 8 | 1 | 0.75789 | 1 | FF-4 120V 1phase 6FLA | 6
| 7 | Light | 23 | 1.44 | 1 | 15 | A | 1 | 1 | 0.021053 | 1 | Access Control | 8
| 9 | Wifi | 6 | 0.082105 | 1 | 1 | B | [5 empty] | 6
| 11 | Intercom | 4 | 0.021053 | 1 | 1 | C | [5 empty] | 8
| 13 | Close Circuit Camera | 4 | 0.023158 | 1 | 1 | A | [5 empty] | 10
| 15 | Barrier free access | 3 | 0.052632 | 1 | 1 | B | [5 empty] | 12
| 17 | Emergency light and exit sign | 5 | 0.018421 | 1 | 1 | C | [5 empty] | 14
| 19 | Push switch | 6 | 0.012632 | 1 | 1 | A | [5 empty] | 16
| 21 | 120V 6FLA FF-1 | 1 | 0.75789 | 1 | 8 | B | [5 empty] | 18
| 23 | Annunciator Panel used as Fire fighter access point | 1 | 0.42105 | 1 | 5 | C | [5 empty] | 20
| 25 | Projector | 1 | 0.42105 | 1 | 5 | A | [5 empty] | 26
| 27 | Computer | 1 | 0.27368 | 1 | 3 | B | [5 empty] | 36
| 29 | Speaker | 1 | 0.23158 | 1 | 3 | C | [5 empty] | 38
| 31 | Receptacles waterproof (15A) | 2 | 3.78 | 1 | 40 | A
| 33 | Light / Sensor light | 32 | 6.4672 | 1 | 68 | B
| 35 | Hand Dryer Automatic | 2 | 0.25263 | 1 | 3 | C
| 37 | Barrier free Access | 1 | 0.052632 | 1 | 1 | A
| 39 | Barrier free Access | 1 | 0.052632 | 1 | 1 | B
| 41 | BBH-8 120V 1phase, 1KW | 1 | 1.0526 | 1 | 11 | C
Load Balance Summary
Sl | Phase | Total Load (KVA)
1 | A | 11.38
2 | B | 11.4
3 | C | 11.95

## 12B
Panel Schedule
Date |  |  |  | Panel ID | 12B |  |  |  |  | Breaker (A) |  | Main Breaker/MLO
Project Name |  |  |  | Mountaining Type | Surface |  |  |  |  | Total Circuit | 44 | ISC Rating
Location |  |  |  | Voltage (V) | 120/208 |  |  |  |  | BUS Rating (A) |  | ISCA (Calculated)
Owner Details |  |  |  | Phase | 3 |  |  |  |  | No. Wire | 4
Note
Room No | Circuit No | Equipments Description | Quantity | Load (KVA) | Pole | Breaker Size | Phase | Breaker Size | Pole | Load (KVA) | Quantity | Equipments Description | Circuit No | Room No
Room 108 | 1 | Receptacles Waterproof (2-20A) | 2 | 3.76 | 1 | 40 | A | 1 | 1 | 0.0053 | 1 | Intercom | 2 | 108
| 3 | Receptacles Waterproof (1-30A/1-15A) | 2 | 3.76 | 1 | 40 | B | [5 empty] | 4
| 5 | Receptacles Waterproof (2-20A) | 2 | 3.76 | 1 | 40 | C | [5 empty] | 6
| 7 | Light | 13 | 0.54737 | 1 | 6 | A | [5 empty] | 8
| 9 | Fridge | 1 | 0.76316 | 1 | 8 | B | [5 empty] | 10
| 11 | Dishwasher | 1 | 1.3684 | 1 | 15 | C | [5 empty] | 12
| 13 | Espresso Machines | 1 | 1.5789 | 1 | 17 | A | [5 empty] | 14
| 15 | Digital Display | 1 | 0.11579 | 1 | 2 | B | [5 empty] | 16
| 17 | Flat top grill | 1 | 0.94 | 3 | 10 | C | [5 empty] | 18
| 19 | Flat top grill | 1 | 0.94 | 3 | 10 | A | [5 empty] | 20
| 21 | Flat top grill | 1 | 0.94 | 3 | 10 | B | [5 empty] | 22
| 23 | Water Purifier | 1 | 0.063158 | 1 | 1 | C | [5 empty] | 24
| 25 | Commercial Oven | 1 | 0.38 | 3 | 4 | A | [5 empty] | 26
| 27 | Commercial Oven | 1 | 0.38 | 3 | 4 | B | [5 empty] | 28
| 29 | Commercial Oven | 1 | 0.38 | 3 | 4 | C | [5 empty] | 30
| 31 | Wifi | 1 | 0.013684 | 1 | 1 | A | [5 empty] | 32
| 33 | BBH-1 | 1 | 2.6316 | 1 | 28 | B | [5 empty] | 34
| 35 | Close Circuit Camera | 2 | 0.011579 | 1 | 1 | C | [5 empty] | 36
| 37 | Emergency light and exit sign | 1 | 0.0036842 | 1 | 1 | A | [5 empty] | 38
| 39 | Exhaust Fan | 1 | 0.00026316 | 1 | 1 | B | [5 empty] | 40
| 41 | BBH-2 | 1 | 1.0526 | 1 | 11 | C | [5 empty] | 42
Load Balance Summary
Sl | Phase | Total Load (KVA)
1 | A | 7.23
2 | B | 8.59
3 | C | 7.58

## 12C
Panel Schedule
Date |  |  |  | Panel ID | [5 empty] | Breaker (A) |  | Main Breaker/MLO
Project Name |  |  |  | Mountaining Type | [5 empty] | Total Circuit |  | ISC Rating
Location |  |  |  | Voltage | [5 empty] | BUS Rating (A) |  | ISCA (Calculated)
Owner Details |  |  |  | Phase | [5 empty] | No. Wire
Note
Room No | Circuit No | Equipments Description | Quantity | Load (KVA) | Pole | Breaker Size | Phase | Breaker Size | Pole | Load (KVA) | Quantity | Equipments Description | Circuit No | Room No
Room 110 | 1 | Receptacles (5-15A) | 5 | 9.4737 | 1 | 99 | A | [5 empty] | 2
| 3 | Light Proper for spotting | 11 | 1.7368 | 1 | 19 | B | [5 empty] | 4
| 5 | Wifi | 1 | 0.013684 | 1 | 1 | C | [5 empty] | 6
| 7 | Intercom | 1 | 0.0052632 | 1 | 1 | A | [5 empty] | 8
| 9 | Close Circuit Camera | 4 | 0.023158 | 1 | 1 | B | [5 empty] | 10
| 11 | Emergency light and exit sign | 1 | 0.0036842 | 1 | 1 | C | [5 empty] | 12
| 13 | Projector | 2 | 0.84211 | 1 | 9 | A | [5 empty] | 14
| 15 | Barrier free access | 1 | 0.052632 | 1 | 1 | B | [5 empty] | 16
| 17 | Push button | 1 | 0.0010526 | 1 | 1 | C | [5 empty] | 18
| 19 | Egress Door | 1 | 0.052632 | 1 | 1 | A | [5 empty] | 20
| 21 | Microphone | 2 | 0.0042105 | 1 | 1 | B | [5 empty] | 22
| 23 | Speaker | 1 | 0.23158 | 1 | 3 | C | [5 empty] | 24
| 25 | BBH-6 1phase 2.5 KW 208 V | 1 | 2.6316 | 1 | 28 | A | [5 empty] | 26
| 27 | BBH-7 1phase 2.5 KW 208 V | 1 | 2.6316 | 1 | 28 | B | [5 empty] | 28
| 29 | Condensing unit,208,3ph,14fla | 1 | 5.0432 | 3 | 53 | C | [5 empty] | 30
| 31 | Condensing unit,208,3ph,18fla | 1 | 6.4842 | 3 | 68 | A | [5 empty] | 32
| 33 | Condensing unit,208,3ph,39fla | 1 | 13.6842 | 3 | 143 | B | [5 empty] | 34
| 35 | Condensing unit,208,3ph,37fla | 1 | 13.3684 | 3 | 140 | C | [5 empty] | 36
| 37 | [11 empty] | 38
| 39 | [11 empty] | 40
| 41 | [11 empty] | 42
Load Balance Summary
|  | Sl | Phase | Total Load (KVA)
|  | 1 | A | 19.33
|  | 2 | B | 18.59
|  | 3 | C | 18.66

## 12D
Panel Schedule
Date |  |  |  | Panel ID | [6 empty] | Breaker (A) |  | Main Breaker/MLO
Project Name |  |  |  | Mountaining Type | [6 empty] | Total Circuit |  | ISC Rating
Location |  |  |  | Voltage | [6 empty] | BUS Rating (A) |  | ISCA (Calculated)
Owner Details |  |  |  | Phase | [6 empty] | No. Wire
Note
Room No | Circuit No | Equipments Description | Quantity | Load (KVA) | Pole | Phase | Breaker Size | Equipments Description | Quantity | Load (KVA) | Pole | Breaker Size | Phase | Circuit No | Room No
109 | 1 | Receptacles ( 15A) | 3 | 5.6893 | 1 | A | 60 | Warming Oven | 1 | 1.0526 | 1 | 11 | A | 2 | 112
109 | 3 | Light | 12 | 0.45474 | 1 | B | 5 | Wifi | 1 | 0.013684 | 1 | 1 | B | 4 | 112
109 | 5 | Wifi | 1 | 0.013684 | 1 | C | 1 | Intercom | 1 | 0.0052632 | 1 | 1 | C | 6 | 112
109 | 7 | Intercom | 1 | 0.0052632 | 1 | A | 1 | Close Circuit Camera | 1 | 0.0057895 | 1 | 1 | A | 8 | 112
109 | 9 | Close Circuit Camera | 4 | 0.023158 | 1 | B | 1 | Emergency light and exit sign | 1 | 0.0036842 | 1 | 1 | B | 10 | 112
109 | 11 | Emergency light and exit sign | 1 | 0.0036842 | 1 | C | 1 | Receptacles (15A) | 1 | 1.8974 | 1 | 20 | C | 14 | 112
109 | 13 | Projector | 2 | 0.84211 | 1 | A | 9 | [6 empty] | 16
109 | 15 | Barrier free access | 1 | 0.052632 | 1 | B | 1 | [6 empty] | 18
109 | 17 | Push button | 2 | 0.0021053 | 1 | C | 1 | [6 empty] | 20
109 | 19 | Egress Door | 1 | 0.052632 | 1 | A | 1 | [6 empty] | 22
109 | 21 | BBH-3 120 V | 1 | 1.0526 | 1 | B | 11 | [6 empty] | 24
109 | 23 | BBH-4 208 V | 1 | 2.6316 | 1 | C | 28 | [6 empty] | 26
109 | 25 | BBH-5 120 V | 1 | 1.0526 | 1 | A | 11 | [6 empty] | 28
109 | 27 | BBH-9 120V | 1 | 1.0526 | 1 | B | 11 | [6 empty] | 30
111 | 29 | Receptacles (15A) | 2 | 3.7894 | 1 | C | 40 | [6 empty] | 32
111 | 31 | Light | 1 | 0.025263 | 1 | A | 1 | [6 empty] | 34
112 | 33 | Receptacles ( 20A) | 3 | 5.6893 | 1 | B | 60 | [6 empty] | 36
112 | 35 | Light | 3 | 0.15158 | 1 | C | 2 | [6 empty] | 38
112 | 37 | Microwave | 1 | 1.0526 | 1 | A | 11 | [6 empty] | 40
112 | 39 | Coffee Machine | 1 | 1.5368 | 1 | B | 17 | [6 empty] | 42
112 | 41 | Fridge | 1 | 0.76316 | 1 | C | 8 | [6 empty] | 44
Load Balance Summary
|  | Sl | Phase | Total Load (KVA)
|  | 1 | A | 9.772
|  | 2 | B | 9.812
|  | 3 | C | 9.324

## 12E
Panel Schedule
Date |  |  |  | Panel ID | 12E |  |  |  |  | Breaker (A) |  | Main Breaker/MLO
Project Name |  |  |  | Mountaining Type | Surface |  |  |  |  | Total Circuit | 42 | ISC Rating
Location |  |  |  | Voltage | 120/208 |  |  |  |  | BUS Rating (A) |  | ISCA (Calculated)
Owner Details |  |  |  | Phase | 3 |  |  |  |  | No. Wire | 4
Note
Room No | Circuit No | Equipments Description | Quantity | Load (KVA) | Pole | Breaker Size | BUS | Breaker Size | Pole | Load (KVA) | Quantity | Equipments Description | Circuit No | Room No
Room - 113 | 1 | Receptacles ( 3-15A) | 3 | 5.6842 | 1 | 60 | A | 40 | 1 | 3.7895 | 2 | Receptacles (2-15A) | 2 | Room - 114
Room - 113 | 3 | Light | 6 | 0.25263 | 1 | 3 | B | 1 | 1 | 0.015789 | 3 | Light | 4 | Room - 114
Room - 113 | 5 | Wifi | 1 | 0.013684 | 1 | 1 | C | 20 | 1 | 1.8947 | 1 | Receptacles (1-15A) | 6 | Room - 115
Room - 113 | 7 | Intercom | 1 | 0.0052632 | 1 | 1 | A | 1 | 1 | 0.063158 | 6 | Light | 8 | Room - 115
Room - 113 | 9 | Close Circuit Camera | 1 | 0.0057895 | 1 | 1 | B | 1 | 1 | 0.052632 | 1 | Climate Controlled | 10 | Room - 115
Room - 113 | 11 | Computer | 1 | 0.27368 | 1 | 3 | C | 79 | 1 | 7.5789 | 4 | Receptacles (4-15A) | 12 | Room - 116
Room - 118 | 13 | Light | 4 | 0.084211 | 1 | 1 | A | 3 | 1 | 0.21053 | 5 | Light | 14 | Room - 116
Room - 118 | 15 | Receptacles (3-15A) | 3 | 5.6842 | 1 | 60 | B | 1 | 1 | 0.013684 | 1 | Wifi | 16 | Room - 116
Room - 118 | 17 | Wifi | 1 | 0.013684 | 1 | 1 | C | 1 | 1 | 0.0052632 | 1 | Intercom | 18 | Room - 116
Room - 118 | 19 | Close Circuit Camera | 1 | 0.0057895 | 1 | 1 | A | 1 | 1 | 0.0057895 | 1 | Close Circuit Camera | 20 | Room - 116
Room - 119 | 21 | Receptacles (1-20A/2-15A) | 3 | 5.6842 | 1 | 60 | B | 1 | 1 | 0.0036842 | 1 | Emergency light and exit sign | 22 | Room - 116
Room - 119 | 23 | Light | 5 | 0.21053 | 1 | 3 | C | 6 | 1 | 0.54737 | 2 | Computer | 24 | Room - 116
Room - 119 | 25 | Printer, Scanner, Copier | 1 | 0.52632 | 1 | 6 | A | 6 | 1 | 0.52632 | 1 | Printer, Scanner, Copier | 26 | Room - 116
Room - 119 | 27 | Intercom | 1 | 0.0052632 | 1 | 1 | B | 1 | 1 | 0.0057895 | 1 | Close Circuit Camera | 28 | Room - 119
Room - 119 | 29 | Wifi | 1 | 0.013684 | 1 | 1 | C | 1 | 1 | 0.0036842 | 1 | Emergency light and exit sign | 30 | Room - 119
Room - 119 | 31 | Computer | 2 | 0.54737 | 1 | 6 | A | 0 | 1 |  |  |  | 32
Room - 119 | 33 | [11 empty] | 34
Room - 119 | 35 | [11 empty] | 36
Room - 119 | 37 | [11 empty] | 38
Room - 119 | 39 | [11 empty] | 40
Room - 119 | 41 | [11 empty] | 42
Room - 119 | 43 | [11 empty] | 44
Load Balance Summary
Sl | Phase | Total Load (KVA)
1 | A | 11.45
2 | B | 11.72
3 | C | 10.56

## 12F
Panel Schedule
Date |  |  |  | Panel ID | 12F |  |  |  |  | Breaker (A) |  | Main Breaker/MLO
Project Name |  |  |  | Mountaining Type | Surface |  |  |  |  | Total Circuit | 42 | ISC Rating
Location |  |  |  | Voltage | 120/208 |  |  |  |  | BUS Rating (A) |  | ISCA (Calculated)
Owner Details |  |  |  | Phase | 3 |  |  |  |  | No. Wire | 4
Note
Room No | Circuit No | Equipments Description | Quantity | Load (KVA) | Pole | Breaker Size | BUS | Breaker Size | Pole | Load (KVA) | Quantity | Equipments Description | Circuit No | Room No
117 | 1 | force flow fan,120V,1ph,1.5KW FF3 | 1 | 1.5789 | 1 | 17 | A | [5 empty] | 2
| 3 | Receptacles (1-20A) | 1 | 1.89 | 1 | 20 | B | [5 empty] | 4
| 5 | Receptacles (1-15A) | 1 | 1.89 | 1 | 20 | C | [5 empty] | 6
| 7 | force flow fan,120V,1ph,1.5KW FF3 | 1 | 1.5789 | 1 | 17 | A | [5 empty] | 8
| 9 | Light | 6 | 0.063158 | 1 | 1 | B | [5 empty] | 10
| 11 | Access Control | 1 | 0.021053 | 1 | 1 | C | [5 empty] | 12
| 13 | furnace,208,3ph,10fla F-1, F-2(2) | 1 | 1.2 | 3 | 13 | A | [5 empty] | 14
| 15 | furnace,208,3ph,10fla F-1, F-2(2) | 1 | 1.2 | 3 | 13 | B | [5 empty] | 16
| 17 | furnace,208,3ph,10fla F-1, F-2(2) | 1 | 1.2 | 3 | 13 | C | [5 empty] | 18
| 19 | Wifi | 1 | 0.013684 | 1 | 1 | A | [5 empty] | 20
| 21 | Intercom | 1 | 0.0052632 | 1 | 1 | B | [5 empty] | 22
| 23 | Emergency light and exit sign | 1 | 0.0036842 | 1 | 1 | C | [5 empty] | 24
| 25 | [11 empty] | 26
| 27 | [11 empty] | 28
| 29 | [11 empty] | 30
| 31 | [11 empty] | 32
| 33 | [11 empty] | 34
| 35 | [11 empty] | 36
| 37 | [11 empty] | 38
| 39 | [11 empty] | 40
| 41 | [11 empty] | 42
Load Balance Summary
Sl | Phase | Total Load (KVA)
1 | A | 4.37
2 | B | 3.15
3 | C | 3.11

## 12G
Panel Schedule
Date |  |  |  | Panel ID | 12G |  |  |  |  | Breaker (A) |  | Main Breaker/MLO
Project Name |  |  |  | Mountaining Type | Surface |  |  |  |  | Total Circuit | 42 | ISC Rating
Location |  |  |  | Voltage | 120/208 |  |  |  |  | BUS Rating (A) |  | ISCA (Calculated)
Owner Details |  |  |  | Phase | 3 |  |  |  |  | No. Wire | 4
Note
Room No | Circuit No | Equipments Description | Quantity | Load (KVA) | Pole | Breaker Size | BUS | Breaker Size | Pole | Load (KVA) | Quantity | Equipments Description | Circuit No | Room No
Room - 120 | 1 | Light | 5 | 0.052632 | 1 | 1 | A | 79 | 1 | 7.5789 | 4 | Receptacles (4-15A) | 2 | Room - 121
Room - 120 | 3 | Receptacles (2-15A) | 2 | 3.7895 | 1 | 40 | B | 1 | 1 | 0.013684 | 1 | Wifi | 4 | Room - 121
Room - 120 | 5 | Wifi | 1 | 0.013684 | 1 | 1 | C | 4 | 1 | 0.37895 | 9 | Light | 6 | Room - 121
Room - 120 | 7 | Intercom | 1 | 0.0052632 | 1 | 1 | A | 1 | 1 | 0.0052632 | 1 | Intercom | 8 | Room - 121
Room - 120 | 9 | Close Circuit Camera | 1 | 0.0057895 | 1 | 1 | B | 1 | 1 | 0.0036842 | 1 | Emergency light and exit sign | 10 | Room - 121
Room - 120 | 11 | Emergency light and exit sign | 1 | 0.0036842 | 1 | 1 | C | 3 | 1 | 0.27368 | 1 | Computer | 12 | Room - 121
Room - 120 | 13 | Access Control | 1 | 0.021053 | 1 | 1 | A | 1 | 1 | 0.011579 | 2 | Close Circuit Camera | 14 | Room - 121
Room - 120 | 15 | exhaust fan,208,3ph,1.5HP | 1 | 0.393 | 3 | 5 | B | 5 | 1 | 0.42105 | 1 | Projector | 16 | Room - 121
Room - 120 | 17 | exhaust fan,208,3ph,1.5HP | 1 | 0.393 | 3 | 5 | C | 9 | 1 | 0.84211 | 1 | Sound System | 18 | Room - 121
Room - 120 | 19 | exhaust fan,208,3ph,1.5HP | 1 | 0.393 | 3 | 5 | A | 2 | 1 | 0.12632 | 6 | Spot Light | 20 | Room - 122
Room - 120 | 21 | force flow fan,120V,1ph, 1.5KW FF-2 | 1 | 1.5789 | 1 | 17 | B | 4 | 1 | 0.33684 | 16 | Light | 22 | Room - 122
Room - 123 | 23 | Light Minimal | 4 | 0.15158 | 1 | 2 | C | 60 | 1 | 5.6842 | 3 | Receptacles (3-15A) | 24 | Room - 122
Room - 123 | 25 | Wifi | 1 | 0.013684 | 1 | 1 | A | 1 | 1 | 0.013684 | 1 | Wifi | 26 | Room - 122
Room - 123 | 27 | Receptacles (1-15A) | 1 | 1.8947 | 1 | 20 | B | 1 | 1 | 0.0052632 | 1 | Intercom | 28 | Room - 122
Room - 123 | 29 | Sound System | 1 | 0.84211 | 1 | 9 | C | 1 | 1 | 0.011579 | 2 | Close Circuit Camera | 30 | Room - 122
Room - 123 | 31 | Close Circuit Camera | 1 | 0.0057895 | 1 | 1 | A | 5 | 1 | 0.42105 | 1 | Projector | 32 | Room - 122
Room - 122 | 33 | Intercom | 1 | 0.0052632 | 1 | 1 | B | 1 | 1 | 0.0036842 | 1 | Emergency light and exit sign | 34 | Room - 122
| 35 |  |  |  | 1 |  | C | [5 empty] | 36
| 37 |  |  |  | 1 |  | A | [5 empty] | 38
| 39 |  |  |  | 1 |  | B | [5 empty] | 40
| 41 |  |  |  | 1 |  | C | [5 empty] | 42
Load Balance Summary
Sl | Phase | Total Load (KVA)
1 | A | 8.65
2 | B | 8.45
3 | C | 8.59

## M2H
Panel Schedule
Date |  |  |  | Panel ID | M2H |  |  |  |  | Breaker (A) |  | Main Breaker/MLO
Project Name |  |  |  | Mountaining Type | Surface |  |  |  |  | Total Circuit | 42 | ISC Rating
Location |  |  |  | Voltage | 120/208 |  |  |  |  | BUS Rating (A) |  | ISCA (Calculated)
Owner Details |  |  |  | Phase | 3 |  |  |  |  | No. Wire | 4
Note
Room No | Circuit No | Equipments Description | Quantity | Load (KVA) | Pole | Breaker Size | BUS | Breaker Size | Pole | Load (KVA) | Quantity | Equipments Description | Circuit No | Room No
Room - 202 | 1 | Close Circuit Camera | 2 | 0.011579 | 1 | 1 | A | 10 | 1 | 0.88947 | 13 | Light | 2 | Room - 203
Room - 202 | 3 | Light | 27 | 1.5632 | 1 | 17 | B | 3 | 1 | 0.19684 | 1 | Exhaust Fan,120,1ph,0.25HP | 4 | Room - 203
Room - 202 | 5 | Wifi | 1 | 0.013684 | 1 | 1 | C | 13 | 3 | 1.2 | 1 | Furnace,208,3ph,12FLA | 6 | Room - 203
Room - 202 | 7 | Fire Alarm Control Panel | 1 | 1.0105 | 1 | 11 | A | 13 | 3 | 1.2 | 1 | Furnace,208,3ph,12FLA | 8 | Room - 203
Room - 202 | 9 | Receptacles (2-15A) | 2 | 3.7895 | 1 | 40 | B | 13 | 3 | 1.2 | 1 | Furnace,208,3ph,12FLA | 10 | Room - 203
Room - 202 | 11 | Intercom | 1 | 0.0052632 | 1 | 1 | C | 50 | 1 | 4.7368 | 1 | Domestic hot water tank,120V,1ph 5FLA | 12 | Room - 203
Room - 202 | 13 | Fire Pump (30 HP) | 1 | 7.85 | 3 | 82 | A | 1 | 1 | 0.013684 | 1 | Wifi | 14 | Room - 203
Room - 202 | 15 | Fire Pump (30 HP) | 1 | 7.85 | 3 | 82 | B | 1 | 1 | 0.0052632 | 1 | Intercom | 16 | Room - 203
Room - 202 | 17 | Fire Pump (30 HP) | 1 | 7.85 | 3 | 82 | C | 1 | 1 | 0.011579 | 2 | Close Circuit Camera | 18 | Room - 203
Room - 202 | 19 | Fire Alarm Booster panel | 1 | 0.63158 | 1 | 7 | A | 60 | 1 | 5.6842 | 3 | Receptacles (3-15A) | 20 | Room - 204
Room - 202 | 21 | Emergency light and exit sign | 1 | 0.0036842 | 1 | 1 | B | 20 | 1 | 1.8274 | 31 | Light | 22 | Room - 204
Room - 203 | 23 | Receptacles (2-15A) | 2 | 3.7895 | 1 | 40 | C | 1 | 1 | 0.013684 | 1 | Wifi | 24 | Room - 204
Room - 203 | 25 | Furnace,208,3ph,10FLA | 1 | 1.2 | 3 | 13 | A | 1 | 1 | 0.0052632 | 1 | Intercom | 26 | Room - 204
Room - 203 | 27 | Furnace,208,3ph,10FLA | 1 | 1.2 | 3 | 13 | B | 1 | 1 | 0.0057895 | 1 | Close Circuit Camera | 28 | Room - 204
Room - 203 | 29 | Furnace,208,3ph,10FLA | 1 | 1.2 | 3 | 13 | C | 3 | 1 | 0.27368 | 1 | Computer | 30 | Room - 204
| 31 | [11 empty] | 32
| 33 | [11 empty] | 34
| 35 | [11 empty] | 36
| 37 | [11 empty] | 38
| 39 | [11 empty] | 40
| 41 | [11 empty] | 42
Load Balance Summary
| Sl | Phase | Total Load (KVA)
| 1 | A | 18.5
| 2 | B | 17.64
| 3 | C | 19.1