## Total Load
Sl. | Room name | Room no. | Equipment | Quantity | LOAD Per Quantity (W) | Total Load ( KW) | voltage | Current (A) | Apparent (KVA | phase | power factor | Total Load (Per Room_KW) | Load Type (Continous/Discont.) | Total Load (Building_kW)
1 | Foyer | Room 100 | [9 empty] | 4.8445
| Foyer | Room 100 | Receptacles (2-15A) | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95
| Foyer | Room 100 | Light | 1 | 40 | 0.04 | 24 | 1.7544 | 0.042105 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | Close Circuit Camera | 2 | 5.5 | 0.011 | 12 | 0.96491 | 0.011579 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | Barrier free access | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | Push switch | 2 | 1 | 0.002 | 24 | 0.087719 | 0.0021053 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | 120V 6FLA FF-1 | 1 | 720 | 0.72 | 120 | 6.3158 | 0.75789 | 1 | 0.95 |  | Continous
| Foyer | Room 100 | Annunciator Panel used as Fire fighter access point | 1 | 400 | 0.4 | 120 | 3.5088 | 0.42105 | 1 | 0.95 |  | Continous
2 | Classroom | Room 101 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 8.467 | Discontinous
| Classroom | Room 101 | Receptacles (4-15A) | 4 | 1800 | 7.2 | 120 | 63.1579 | 7.5789 | 1 | 0.95 |  | Discontinous
| Classroom | Room 101 | Light | 9 | 40 | 0.36 | 120 | 3.1579 | 0.37895 | 1 | 0.95 |  | Continous
| Classroom | Room 101 | Projector | 1 | 400 | 0.4 | 120 | 3.5088 | 0.42105 | 1 | 0.95 |  | Discontinous
| Classroom | Room 101 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Classroom | Room 101 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Classroom | Room 101 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
| Classroom | Room 101 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Classroom | Room 101 | Computer | 1 | 260 | 0.26 | 120 | 2.2807 | 0.27368 | 1 | 0.95 |  | Discontinous
| Classroom | Room 101 | Speaker | 1 | 220 | 0.22 | 120 | 1.9298 | 0.23158 | 1 | 0.95 |  | Discontinous
3 | Closet | Room 102 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 3.624 | Discontinous
| Closet | Room 102 | Receptacles | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95 |  | Discontinous
| Closet | Room 102 | Light | 4 | 6 | 0.024 | 120 | 0.21053 | 0.025263 | 1 | 0.95 |  | Continous
4 | W. Washrrom | Room 103 | [5 empty] | #DIV/0! | 0 | 1 | 0.95 | 7.2605 | Discontinous
| W. Washrrom | Room 103 | Receptacles waterproof (3-15A) | 3 | 1800 | 5.4 | 120 | 47.3684 | 5.6842 | 1 | 0.95 |  | Discontinous
| W. Washrrom | Room 103 | Light / Sensor light | 16 | 12 | 0.192 | 120 | 1.6842 | 0.20211 | 1 | 0.95 |  | Continous
| W. Washrrom | Room 103 | Hand Dryer Automatic | 1 | 1600 | 1.6 | 120 | 14.0351 | 1.6842 | 1 | 0.95 |  | Discontinous
| W. Washrrom | Room 103 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| W. Washrrom | Room 103 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| W. Washrrom | Room 103 | Barrier free Access | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| W. Washrrom | Room 103 | Push Switch | 2 | 1 | 0.002 | 24 | 0.087719 | 0.0021053 | 1 | 0.95 |  | Continous
5 | M. Washroom | Room 104 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 3.0725 | Discontinous | 250.6398
| M. Washroom | Room 104 | Receptacles waterproof (1-15A) | 1 | 1800 | 1.8 | 120 | 15.7895 | 1.8947 | 1 | 0.95 |  | Discontinous
| M. Washroom | Room 104 | Light / Sensor light | 7 | 12 | 0.084 | 120 | 0.73684 | 0.088421 | 1 | 0.95 |  | Continous
| M. Washroom | Room 104 | Hand Dryer Automatic | 1 | 120 | 0.12 | 120 | 1.0526 | 0.12632 | 1 | 0.95 |  | Discontinous
| M. Washroom | Room 104 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| M. Washroom | Room 104 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| M. Washroom | Room 104 | Barrier free Access | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| M. Washroom | Room 104 | Push Switch | 2 | 1 | 0.002 | 24 | 0.087719 | 0.0021053 | 1 | 0.95 |  | Continous
| M. Washroom | Room 104 | BBH-8 120V 1phase, 1KW | 1 | 1000 | 1 | 120 | 8.7719 | 1.0526 | 1 | 0.95 |  | Continous
6 | Washroom Corridor | Room 105 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 0.0275 | Discontinous
| Washroom Corridor | Room 105 | Light | 2 | 3 | 0.006 | 120 | 0.052632 | 0.0063158 | 1 | 0.95 |  | Continous
| Washroom Corridor | Room 105 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Washroom Corridor | Room 105 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Washroom Corridor | Room 105 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
7 | Janitor | Room 106 | Receptacles (1-20A) | 1 | 1800 | 1.8 | 120 | 15.7895 | 1.8947 | 1 | 0.95 | 1.818 | Discontinous
| Janitor | Room 106 | Light | 2 | 9 | 0.018 | 120 | 0.15789 | 0.018947 | 1 | 0.95 |  | Continous
8 | Water Meter | Room 107 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 0.75 | Discontinous
| Water Meter | Room 107 | Light | 1 | 10 | 0.01 | 120 | 0.087719 | 0.010526 | 1 | 0.95 |  | Continous
| Water Meter | Room 107 | Sprinkler Flow Switch and Temper Switch1 | 1 | 20 | 0.02 | 120 | 0.17544 | 0.021053 | 1 | 0.95 |  | Discontinous
| Water Meter | Room 107 | FF-4 120V 1phase 6FLA | 1 | 720 | 0.72 | 120 | 6.3158 | 0.75789 | 1 | 0.95 |  | Continous
9 | Catering Kicthenette | Room 108 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 22.3478 | Discontinous
| Catering Kicthenette | Room 108 | Receptacles Waterproof (4-20A/ 1-30A/1-15A) | 6 | 1800 | 10.8 | 120 | 94.7368 | 11.3684 | 1 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Light | 13 | 40 | 0.52 | 120 | 4.5614 | 0.54737 | 1 | 0.95 |  | Continous
| Catering Kicthenette | Room 108 | Fridge | 1 | 725 | 0.725 | 120 | 6.3596 | 0.76316 | 1 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Dishwasher | 1 | 1300 | 1.3 | 120 | 11.4035 | 1.3684 | 1 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Espresso Machines | 1 | 1500 | 1.5 | 120 | 13.1579 | 1.5789 | 1 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Digital Display | 1 | 110 | 0.11 | 120 | 0.96491 | 0.11579 | 1 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Flat top grill | 1 | 2700 | 2.7 | 208 | 13.664 | 2.8421 | 3 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Water Purifier | 1 | 60 | 0.06 | 120 | 0.52632 | 0.063158 | 1 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Commercial Oven | 1 | 1100 | 1.1 | 208 | 5.5668 | 1.1579 | 3 | 0.95 |  | Discontinous
| Catering Kicthenette | Room 108 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Catering Kicthenette | Room 108 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Catering Kicthenette | Room 108 | Close Circuit Camera | 2 | 5.5 | 0.011 | 12 | 0.96491 | 0.011579 | 1 | 0.95 |  | Continous
| Catering Kicthenette | Room 108 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Catering Kicthenette | Room 108 | Exhaust Fan | 1 | 0.25 | 0.00025 | 120 | 0.002193 | 0.00026316 | 1 | 0.95 |  | Continous
| Catering Kicthenette | Room 108 | BBH-1 | 1 | 2500 | 2.5 | 208 | 12.6518 | 2.6316 | 1 | 0.95 |  | Continous
| Catering Kicthenette | Room 108 | BBH-2 | 1 | 1000 | 1 | 120 | 8.7719 | 1.0526 | 1 | 0.95 |  | Continous
10 | Commons | Room 109 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 12.2775 | Discontinous
| Commons | Room 109 | Receptacles ( 3-15A) | 3 | 1800 | 5.4 | 120 | 47.3684 | 5.6842 | 1 | 0.95 |  | Discontinous
| Commons | Room 109 | Light | 12 | 36 | 0.432 | 120 | 3.7895 | 0.45474 | 1 | 0.95 |  | Continous
| Commons | Room 109 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Commons | Room 109 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Commons | Room 109 | Close Circuit Camera | 4 | 5.5 | 0.022 | 12 | 1.9298 | 0.023158 | 1 | 0.95 |  | Continous
| Commons | Room 109 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Commons | Room 109 | Projector | 2 | 400 | 0.8 | 120 | 7.0175 | 0.84211 | 1 | 0.95 |  | Discontinous
| Commons | Room 109 | Barrier free access | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| Commons | Room 109 | Push button | 2 | 1 | 0.002 | 24 | 0.087719 | 0.0021053 | 1 | 0.95 |  | Continous
| Commons | Room 109 | Egress Door | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| Commons | Room 109 | BBH-3 120 V | 1 | 1000 | 1 | 120 | 8.7719 | 1.0526 | 1 | 0.95 |  | Continous
| Commons | Room 109 | BBH-4 208 V | 1 | 2500 | 2.5 | 208 | 12.6518 | 2.6316 | 1 | 0.95 |  | Continous
| Commons | Room 109 | BBH-5 120 V | 1 | 1000 | 1 | 120 | 8.7719 | 1.0526 | 1 | 0.95 |  | Continous
| Commons | Room 109 | BBH-9 120V | 1 | 1000 | 1 | 120 | 8.7719 | 1.0526 | 1 | 0.95 |  | Continous
11 | Cultural Room | Room 110 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 53.4695 | Discontinous
| Cultural Room | Room 110 | Receptacles (5-15A) | 5 | 1800 | 9 | 120 | 78.9474 | 9.4737 | 1 | 0.95 |  | Discontinous
| Cultural Room | Room 110 | Light Proper for spotting | 11 | 150 | 1.65 | 120 | 14.4737 | 1.7368 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Close Circuit Camera | 4 | 5.5 | 0.022 | 12 | 1.9298 | 0.023158 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Projector | 2 | 400 | 0.8 | 120 | 7.0175 | 0.84211 | 1 | 0.95 |  | Discontinous
| Cultural Room | Room 110 | Barrier free access | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Push button | 1 | 1 | 0.001 | 24 | 0.04386 | 0.0010526 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Egress Door | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | Microphone | 2 | 2 | 0.004 | 12 | 0.35088 | 0.0042105 | 1 | 0.95 |  | Discontinous
| Cultural Room | Room 110 | Speaker | 1 | 220 | 0.22 | 120 | 1.9298 | 0.23158 | 1 | 0.95 |  | Discontinous
| Cultural Room | Room 110 | BBH-6 1phase 2.5 KW 208 V | 1 | 2500 | 2.5 | 208 | 12.6518 | 2.6316 | 1 | 0.95 |  | Continous
| Cultural Room | Room 110 | BBH-7 1phase 2.5 KW 208 V | 1 | 2500 | 2.5 | 208 | 12.6518 | 2.6316 | 1 | 0.95 |  | Continous
| Exterior Sub of Culture | Room 110 | Condensing unit,208,3ph,14fla | 1 | 4791 | 4.791 | 208 | 24.246 | 5.0432 | 3 | 0.95 |  | Continous
| Exterior Sub of Culture | Room 110 | Condensing unit,208,3ph,18fla | 1 | 6160 | 6.16 | 208 | 31.1741 | 6.4842 | 3 | 0.95 |  | Continous
| Exterior Sub of Culture | Room 110 | Condensing unit,208,3ph,39fla | 1 | 13000 | 13 | 208 | 65.7895 | 13.6842 | 3 | 0.95 |  | Continous
| Exterior Sub of Culture | Room 110 | Condensing unit,208,3ph,37fla | 1 | 12700 | 12.7 | 208 | 64.2713 | 13.3684 | 3 | 0.95 |  | Continous
12 | Storage | Room 111 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 3.624 | Discontinous
| Storage | Room 111 | Receptacles (2-15A) | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95 |  | Discontinous
| Storage | Room 111 | Light | 1 | 24 | 0.024 | 120 | 0.21053 | 0.025263 | 1 | 0.95 |  | Continous
13 | Snack | Room 112 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 11.556 | Discontinous
| Snack | Room 112 | Receptacles (1-15A/ 3-20A) | 4 | 1800 | 7.2 | 120 | 63.1579 | 7.5789 | 1 | 0.95 |  | Discontinous
| Snack | Room 112 | Light | 3 | 48 | 0.144 | 120 | 1.2632 | 0.15158 | 1 | 0.95 |  | Continous
| Snack | Room 112 | Microwave | 1 | 1000 | 1 | 120 | 8.7719 | 1.0526 | 1 | 0.95 |  | Discontinous
| Snack | Room 112 | Coffee Machine | 1 | 1460 | 1.46 | 120 | 12.807 | 1.5368 | 1 | 0.95 |  | Discontinous
| Snack | Room 112 | Fridge | 1 | 725 | 0.725 | 120 | 6.3596 | 0.76316 | 1 | 0.95 |  | Discontinous
| Snack | Room 112 | Warming Oven | 1 | 1000 | 1 | 120 | 8.7719 | 1.0526 | 1 | 0.95 |  | Discontinous
| Snack | Room 112 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Snack | Room 112 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Snack | Room 112 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
| Snack | Room 112 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
14 | Information | Room 113 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 5.9235 | Discontinous
| Information | Room 113 | Receptacles ( 3-15A) | 3 | 1800 | 5.4 | 120 | 47.3684 | 5.6842 | 1 | 0.95 |  | Discontinous
| Information | Room 113 | Light | 6 | 40 | 0.24 | 120 | 2.1053 | 0.25263 | 1 | 0.95 |  | Continous
| Information | Room 113 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Information | Room 113 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Information | Room 113 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
| Information | Room 113 | Computer | 1 | 260 | 0.26 | 120 | 2.2807 | 0.27368 | 1 | 0.95 |  | Discontinous
15 | Room 114 | Room 114 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 3.615 | Discontinous
| Room 114 | Room 114 | Receptacles (2-15A) | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95 |  | Discontinous
| Room 114 | Room 114 | Light | 3 | 5 | 0.015 | 120 | 0.13158 | 0.015789 | 1 | 0.95 |  | Continous
16 | Yukuta | Room 115 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 1.91 | Discontinous
| Yukuta | Room 115 | Receptacles (1-15A) | 1 | 1800 | 1.8 | 120 | 15.7895 | 1.8947 | 1 | 0.95 |  | Discontinous
| Yukuta | Room 115 | Light | 6 | 10 | 0.06 | 120 | 0.52632 | 0.063158 | 1 | 0.95 |  | Continous
| Yukuta | Room 115 | Climate Controlled | 1 | 50 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
17 | Education | Room 116 |  |  |  | 0 |  | #DIV/0! | 0 | 1 | 0.95 | 8.447 | Discontinous
| Education | Room 116 | Receptacles (3-15A/ 1-15A) | 4 | 1800 | 7.2 | 120 | 63.1579 | 7.5789 | 1 | 0.95 |  | Discontinous
| Education | Room 116 | Light | 5 | 40 | 0.2 | 120 | 1.7544 | 0.21053 | 1 | 0.95 |  | Continous
| Education | Room 116 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Education | Room 116 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Education | Room 116 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
| Education | Room 116 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Education | Room 116 | Computer | 2 | 260 | 0.52 | 120 | 4.5614 | 0.54737 | 1 | 0.95 |  | Discontinous
| Education | Room 116 | Printer, Scanner, Copier | 1 | 500 | 0.5 | 120 | 4.386 | 0.52632 | 1 | 0.95 |  | Discontinous
18 | Mechanical | Room 117 |  |  |  | 0 |  | #DIV/0! | #DIV/0! |  |  | 8.624 | Discontinous
| Mechanical | Room 117 | Receptacles (1-20A/1-15A) | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95 |  | Discontinous
| Mechanical | Room 117 | Light | 6 | 10 | 0.06 | 120 | 0.52632 | 0.063158 | 1 | 0.95 |  | Continous
| Mechanical | Room 117 | Access Control | 1 | 20 | 0.02 | 120 | 0.17544 | 0.021053 | 1 | 0.95 |  | Continous
| Mechanical | Room 117 | force flow fan,120V,1ph,1.5KW FF3 | 1 | 1500 | 1.5 | 120 | 13.1579 | 1.5789 | 1 | 0.95 |  | Continous
| Mechanical | Room 117 | furnace,208,3ph,10fla F-1, F-2(2) | 1 | 3422.5 | 3.4225 | 208 | 17.3203 | 3.6026 | 3 | 0.95 |  | Continous
| Mechanical | Room 117 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Mechanical | Room 117 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Mechanical | Room 117 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
19 | Staff | Room 118 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 5.4985 | Discontinous
| Staff | Room 118 | Receptacles (3-15A) | 3 | 1800 | 5.4 | 120 | 47.3684 | 5.6842 | 1 | 0.95 |  | Discontinous
| Staff | Room 118 | Light | 4 | 20 | 0.08 | 120 | 0.70175 | 0.084211 | 1 | 0.95 |  | Continous
| Staff | Room 118 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Staff | Room 118 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
20 | Administration | Room 119 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 6.647 | Discontinous
| Administration | Room 119 | Receptacles (1-20A/2-15A) | 3 | 1800 | 5.4 | 120 | 47.3684 | 5.6842 | 1 | 0.95 |  | Discontinous
| Administration | Room 119 | Light | 5 | 40 | 0.2 | 120 | 1.7544 | 0.21053 | 1 | 0.95 |  | Continous
| Administration | Room 119 | Computer | 2 | 260 | 0.52 | 120 | 4.5614 | 0.54737 | 1 | 0.95 |  | Discontinous
| Administration | Room 119 | Printer, Scanner, Copier | 1 | 500 | 0.5 | 120 | 4.386 | 0.52632 | 1 | 0.95 |  | Discontinous
| Administration | Room 119 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Administration | Room 119 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Administration | Room 119 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
| Administration | Room 119 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
21 | Vestibule | Room 120 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 6.317 | Discontinous
| Vestibule | Room 120 | Receptacles (2-15A) | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95 |  | Discontinous
| Vestibule | Room 120 | Light | 5 | 10 | 0.05 | 120 | 0.4386 | 0.052632 | 1 | 0.95 |  | Continous
| Vestibule | Room 120 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Vestibule | Room 120 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Vestibule | Room 120 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
| Vestibule | Room 120 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Vestibule | Room 120 | Access Control | 1 | 20 | 0.02 | 120 | 0.17544 | 0.021053 | 1 | 0.95 |  | Continous
| Vestibule | Room 120 | exhaust fan,208,3ph,1.5HP | 1 | 1120 | 1.12 | 208 | 5.668 | 1.1789 | 3 | 0.95 |  | Continous
| Vestibule | Room 120 | force flow fan,120V,1ph, 1.5KW FF-2 | 1 | 1500 | 1.5 | 120 | 13.1579 | 1.5789 | 1 | 0.95 |  | Continous
22 | Classroom | Room 121 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 9.0525 | Discontinous
| Classroom | Room 121 | Receptacles (4-15A) | 4 | 1800 | 7.2 | 120 | 63.1579 | 7.5789 | 1 | 0.95 |  | Discontinous
| Classroom | Room 121 | Light | 9 | 40 | 0.36 | 120 | 3.1579 | 0.37895 | 1 | 0.95 |  | Continous
| Classroom | Room 121 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Classroom | Room 121 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Classroom | Room 121 | Close Circuit Camera | 2 | 5.5 | 0.011 | 12 | 0.96491 | 0.011579 | 1 | 0.95 |  | Continous
| Classroom | Room 121 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Classroom | Room 121 | Computer | 1 | 260 | 0.26 | 120 | 2.2807 | 0.27368 | 1 | 0.95 |  | Discontinous
| Classroom | Room 121 | Projector | 1 | 400 | 0.4 | 120 | 3.5088 | 0.42105 | 1 | 0.95 |  | Discontinous
| Classroom | Room 121 | Sound System | 1 | 800 | 0.8 | 120 | 7.0175 | 0.84211 | 1 | 0.95 |  | Discontinous
23 | Exhibit | Room 122 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 6.9525 | Discontinous
| Exhibit | Room 122 | Receptacles (3-15A) | 3 | 1800 | 5.4 | 120 | 47.3684 | 5.6842 | 1 | 0.95 |  | Discontinous
| Exhibit | Room 122 | Light | 10 | 20 | 0.2 | 120 | 1.7544 | 0.21053 | 1 | 0.95 |  | Continous
| Exhibit | Room 122 | Spot Light | 6 | 20 | 0.12 | 120 | 1.0526 | 0.12632 | 1 | 0.95 |  | Continous
| Exhibit | Room 122 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Exhibit | Room 122 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Exhibit | Room 122 | Close Circuit Camera | 2 | 5.5 | 0.011 | 12 | 0.96491 | 0.011579 | 1 | 0.95 |  | Continous
| Exhibit | Room 122 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
| Exhibit | Room 122 | Projector | 1 | 400 | 0.4 | 120 | 3.5088 | 0.42105 | 1 | 0.95 |  | Discontinous
| Exhibit | Room 122 | Sound System | 1 | 800 | 0.8 | 120 | 7.0175 | 0.84211 | 1 | 0.95 |  | Discontinous
24 | Tea | Room 123 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 1.9675 | Discontinous
| Tea | Room 123 | Receptacles (1-15A) | 1 | 1800 | 1.8 | 120 | 15.7895 | 1.8947 | 1 | 0.95 |  | Discontinous
| Tea | Room 123 | Light Minimal | 4 | 36 | 0.144 | 120 | 1.2632 | 0.15158 | 1 | 0.95 |  | Continous
| Tea | Room 123 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Tea | Room 123 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Tea | Room 123 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
25 | Stairwell | Room 200 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 0.0635 | Discontinous
| Stairwell | Room 200 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 |  | Discontinous
| Stairwell | Room 200 | Light | 2 | 10 | 0.02 | 120 | 0.17544 | 0.021053 | 1 | 0.95 |  | Continous
| Stairwell | Room 200 | Access Control | 1 | 20 | 0.02 | 120 | 0.17544 | 0.021053 | 1 | 0.95 |  | Continous
| Stairwell | Room 200 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Stairwell | Room 200 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Stairwell | Room 200 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
26 | Electrical | Room 202 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 29.0575 | Discontinous
| Electrical | Room 202 | Receptacles (2-15A) | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95 |  | Discontinous
| Electrical | Room 202 | Light | 27 | 55 | 1.485 | 120 | 13.0263 | 1.5632 | 1 | 0.95 |  | Continous
| Electrical | Room 202 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Electrical | Room 202 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Electrical | Room 202 | Close Circuit Camera | 2 | 5.5 | 0.011 | 12 | 0.96491 | 0.011579 | 1 | 0.95 |  | Continous
| Electrical | Room 202 | Fire Alarm Control Panel | 1 | 960 | 0.96 | 120 | 8.4211 | 1.0105 | 1 | 0.95 |  | Continous
| Electrical | Room 202 | Fire Pump (30 HP) | 1 | 22380 | 22.38 | 208 | 113.2591 | 23.5579 | 3 | 0.95 |  | Continous
| Electrical | Room 202 | Fire Alarm Booster panel | 1 | 600 | 0.6 | 120 | 5.2632 | 0.63158 | 1 | 0.95 |  | Continous
| Electrical | Room 202 | Emergency light and exit sign | 1 | 3.5 | 0.0035 | 120 | 0.030702 | 0.0036842 | 1 | 0.95 |  | Continous
27 | Mechanical | Room 203 |  |  |  | 0 |  | #DIV/0! | #DIV/0! |  |  | 16.006 | Discontinous
| Mechanical | Room 203 | Receptacles (2-15A) | 2 | 1800 | 3.6 | 120 | 31.5789 | 3.7895 | 1 | 0.95 |  | Discontinous
| Mechanical | Room 203 | Light | 13 | 65 | 0.845 | 120 | 7.4123 | 0.88947 | 1 | 0.95 |  | Continous
| Mechanical | Room 203 | Exhaust Fan,120,1ph,0.25HP | 1 | 187 | 0.187 | 120 | 1.6404 | 0.19684 | 1 | 0.95 |  | Continous
| Mechanical | Room 203 | Furnace,208,3ph,10FLA | 1 | 3422.5 | 3.4225 | 208 | 17.3203 | 3.6026 | 3 | 0.95 |  | Continous
| Mechanical | Room 203 | Furnace,208,3ph,12FLA | 1 | 3422.5 | 3.4225 | 208 | 17.3203 | 3.6026 | 3 | 0.95 |  | Continous
| Mechanical | Room 203 | Domestic hot water tank,120V,1ph 5FLA | 1 | 4500 | 4.5 | 240 | 19.7368 | 4.7368 | 1 | 0.95 |  | Continous
| Mechanical | Room 203 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Mechanical | Room 203 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Mechanical | Room 203 | Close Circuit Camera | 2 | 5.5 | 0.011 | 12 | 0.96491 | 0.011579 | 1 | 0.95 |  | Continous
28 | Telecom | Room 204 |  |  |  | 0 |  | #DIV/0! | 0 |  | 0.95 | 7.4195 | Discontinous
| Telecom | Room 204 | Receptacles (3-15A) | 3 | 1800 | 5.4 | 120 | 47.3684 | 5.6842 | 1 | 0.95 |  | Discontinous
| Telecom | Room 204 | Light | 31 | 56 | 1.736 | 120 | 15.2281 | 1.8274 | 1 | 0.95 |  | Continous
| Telecom | Room 204 | Wifi | 1 | 13 | 0.013 | 48 | 0.28509 | 0.013684 | 1 | 0.95 |  | Continous
| Telecom | Room 204 | Intercom | 1 | 5 | 0.005 | 24 | 0.2193 | 0.0052632 | 1 | 0.95 |  | Continous
| Telecom | Room 204 | Close Circuit Camera | 1 | 5.5 | 0.0055 | 12 | 0.48246 | 0.0057895 | 1 | 0.95 |  | Continous
| Telecom | Room 204 | Computer | 1 | 260 | 0.26 | 120 | 2.2807 | 0.27368 | 1 | 0.95 |  | Discontinous

## CPU Connected Load
Sl | Equipment List (Emergency) | Quantity | Avg.Load Per Quantity (W) | Total Load ( KW) | Apparent (KVA | phase | power factor
1 | Wifi | 22 | 13 | 0.286 | 0.30105 | 1 | 0.95
2 | Close Circuit Camera | 30 | 5.5 | 0.165 | 0.17368 | 1 | 0.95
3 | Barrier free access | 5 | 50 | 0.25 | 0.26316 | 1 | 0.95
4 | Emergency light and exit sign | 16 | 3.5 | 0.056 | 0.058947 | 1 | 0.95
5 | Push switch | 6 | 1 | 0.006 | 0.0063158 | 1 | 0.95
6 | Projector | 7 | 400 | 2.8 | 2.9474 | 1 | 0.95
7 | Computer | 8 | 260 | 2.08 | 2.1895 | 1 | 0.95
8 | Speaker | 2 | 220 | 0.44 | 0.46316 | 1 | 0.95
9 | Sprinkler Flow Switch and Temper Switch1 | 1 | 20 | 0.02 | 0.021053 | 1 | 0.95
10 | Push button | 2 | 1 | 0.002 | 0.0021053 | 1 | 0.95
11 | Egress Door | 2 | 50 | 0.1 | 0.10526 | 1 | 0.95
12 | Access Control | 3 | 20 | 0.06 | 0.063158 | 1 | 0.95
13 | Sound System | 2 | 800 | 1.6 | 1.6842 | 1 | 0.95
14 | Fire Alarm Control Panel | 1 | 960 | 0.96 | 1.0105 | 1 | 0.95
15 | Fire Alarm Booster panel | 1 | 600 | 0.6 | 0.63158 | 1 | 0.95
16 | Light | 180 | 28.08 | 7.129 | 7.5042 | 1 | 0.95
Total |  | 288 | 3432.08 | 16.554 | 17.4253

## Sheet4
Summary of UPS and Battery Requirement
Parameter | Value
Total Load | 16.55 kW
Power Factor (PF) | 0.95
Apparent Power (S) | 17.43 kVA
Recommended UPS | 25 kVA
Backup Time | 1 hour
Battery Bank Voltage | 240V
Battery Capacity | 80 Ah
Number of Batteries | 20 (12V, 80Ah each)