## Classroom 121
Length (Inch) | (ft) | meter | Width (Inch) |  | Width (m) | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
2.668 | 21.344 | 6.5057 | 2.05 | 16.4 | 4.9987 | 32.5199 | 375 | 0.4 | 0.9 | 4000 | 8.4687

## Gallery 122
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
2.668 | 21.344 | 6.5057 | 2.11 | 16.88 | 5.145 | 33.4717 | 300 | 0.4 | 0.9 | 1800 | 15.4962

## Tea Ceremony_123
t
| Length (Inch) | (ft) | meter | Width Inch) |  | Width (m) | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
| 2.7 | 21.6 | 6.5837 | 2.1 | 16.8 | 5.1206 | 33.7127 | 150 | 0.4 | 0.9 | 4000 | 3.5117

## Foyer 100
Length (Inch) | (ft) | meter | Width (Inch) |  | Width (m) | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
1.16 | 9.28 | 2.8285 | 0.5 | 4 | 1.2192 | 3.4486 | 375 | 0.4 | 0.9 | 4000 | 0.89806

## Classroom 101
Length (Inch) | (ft) | meter | Width (Inch) |  | Width (m) | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
2.59 | 20.72 | 6.3155 | 2.0606 | 16.4848 | 5.0246 | 31.7324 | 375 | 0.4 | 0.9 | 4000 | 8.2637

## Closet 102
Length (Inch) | (ft) | meter | Width (Inch) |  | Width (m) | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
0.6607 | 5.2856 | 1.6111 | 0.6538 | 5.2304 | 1.5942 | 2.5684 | 150 | 0.4 | 0.9 | 300 | 3.5672

## Womens Washroom 103
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
2.3 | 18.4 | 5.6083 | 1.74 | 13.92 | 4.2428 | 23.7951 | 280 | 0.4 | 0.9 | 1200 | 15.4227

## Mens Washroom_104
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
2.3 | 18.4 | 3.57 | 1.74 | 13.92 | 2.98 | 10.6386 | 280 | 0.4 | 0.9 | 1200 | 6.8954

## Corr 105
Length (Inch) | (ft) | meter | width (Inch) |  | Width (m) | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
0.3754 | 3.0032 | 0.91538 | 0.2972 | 2.3776 | 0.72469 | 0.66337 | 250 | 0.4 | 0.9 | 270 | 1.7062

## Jan 106
Length (Inch) | (ft) | meter | Width (Inch) |  | Width (m) | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
0.6623 | 5.2984 | 1.615 | 0.2819 | 2.2552 | 0.68738 | 1.1101 | 300 | 0.4 | 0.9 | 600 | 1.5418

## Water Meter 107
Length (Inch) | (ft) | meter | Width (Inch) |  | Width (m) | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
0.6607 | 5.2856 | 1.6111 | 0.0206 | 0.1648 | 0.050231 | 0.080925 | 75 | 0.4 | 0.9 | 1000 | 0.016859

## Kitchen 108
Length (Inch) | (ft) | meter | Width (inch) |  | Width (m) | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
2.6533 | 21.2264 | 6.4698 | 2.3247 | 18.5976 | 5.6685 | 36.6744 | 500 | 0.4 | 0.9 | 4000 | 12.7342

## Common 109
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
2.668 | 21.344 | 6.5057 | 2.05 | 16.4 | 4.9987 | 32.5199 | 450 | 0.4 | 0.9 | 3600 | 11.2916
Area = 18.54 inch square

## Culturual 110
Length (Inch) | (ft) | meter | Width (Inch) |  | Width (m) | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
6.0143 | 48.1144 | 14.6653 | 3.025 | 24.2 | 7.3762 | 108.1734 | 750 | 0.4 | 0.9 | 21000 | 10.7315

## Storage 111
Length (Inch) | (ft) | meter | Width (Inch) |  | Width (m) | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
0.9 | 7.2 | 2.1946 | 0.7433 | 5.9464 | 1.8125 | 3.9776 | 100 | 0.4 | 0.9 | 2000 | 0.55244

## Snacks 112
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
2.065 | 16.52 | 5.0353 | 0.98 | 7.84 | 2.3896 | 12.0325 | 350 | 0.4 | 0.9 | 4000 | 2.9246

## Information 113
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
2.095 | 16.76 | 5.1084 | 2.106 | 16.848 | 5.1353 | 26.2333 | 300 | 0.4 | 0.9 | 4000 | 5.4653

## Storage_114
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
0.57 | 4.56 | 1.3899 | 0.445 | 3.56 | 1.0851 | 1.5082 | 200 | 0.4 | 0.9 | 400 | 2.0947

## Yukata 115
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
1.668 | 13.344 | 4.0673 | 0.75 | 6 | 1.8288 | 7.4382 | 200 | 0.4 | 0.9 | 800 | 5.1654

## Education 116
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
1.616 | 12.928 | 3.9405 | 1.44 | 11.52 | 3.5113 | 13.8361 | 500 | 0.4 | 0.9 | 4000 | 4.8042

## Mechanical 117
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
1.15 | 9.2 | 2.8042 | 1.11 | 8.88 | 2.7066 | 7.5898 | 200 | 0.4 | 0.9 | 800 | 5.2707

## Staff lockers 118
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
1.28 | 10.24 | 3.1212 | 0.98 | 7.84 | 2.3896 | 7.4584 | 300 | 0.4 | 0.9 | 2000 | 3.1077

## Administration 119
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
1.61 | 12.88 | 3.9258 | 1.5 | 12 | 3.6576 | 14.3591 | 500 | 0.4 | 0.9 | 4000 | 4.9858

## Vestibule 120
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
1.25 | 10 | 3.048 | 0.61 | 4.88 | 1.4874 | 4.5337 | 300 | 0.4 | 0.9 | 800 | 4.7226

## Power
Length (Inch) | (ft) | meter | Width (Inch) |  | Width (m) | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
2.668 | 21.344 | 6.5057 | 2.05 | 16.4 | 4.9987 | 32.5199 | 375 | 0.4 | 0.9 | 3400 | 9.9632
Not Done

## Stairwell 200
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
1.11 | 8.88 | 2.7066 | 0.387 | 3.096 | 0.94366 | 2.5541 | 150 | 0.4 | 0.9 | 800 | 1.3303

## Electrical 202
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
5.49 | 43.92 | 13.3868 | 4.02 | 32.16 | 9.8024 | 131.2225 | 500 | 0.4 | 0.9 | 7000 | 26.0362

## Mechanical 203
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
5.18 | 41.44 | 12.6309 | 4.6 | 36.8 | 11.2166 | 141.6764 | 250 | 0.4 | 0.9 | 8000 | 12.2983

## Telecom 204
Length (Inch) | (ft) | meter |  |  | Width | Area | Iluminance | Cu | LLF | lume per lumenaries | No.of Lumenaries
5.44 | 43.52 | 13.2649 | 3.22 | 25.76 | 7.8516 | 104.1513 | 750 | 0.4 | 0.9 | 7200 | 30.1364

## Lumen Sum
Lumeniare Feature | Room 100 Foyer | Room 101 Classroom | Room 102 Closet | Room 103 W. Washrrom | Room 104 M. Washroom | Room 105 Washroom Corridor | Room 106 Janitor | Room 107 Water Meter | Room 108 Catering Kicthenette | Room 109 Commons | Room 110 Cultural Room | Room 111 Storage | Room 112 Snack | Room 113 Information | Room 114 | Room 115 Yukuta | Room 116 Education | Room 117 Mechanical | Room 118 Staff | Room 119 Administration | Room 120 Vestibule | Room 121 Classroom | Room 122 Exhibit | Room 123 Tea | Room 200 Stairwell | Room 202 Electrical | Room 203 Mechanical | Room 204 Telecom
Illuminace | 350 | 375 | 150 | 280 | 280 | 250 | 300 | 75 | 500 | 450 | 750 | 100 | 350 | 300 | 200 | 200 | 500 | 200 | 300 | 500 | 300 | 375 | 300 | 150 | 150 | 500 | 250 | 750
number of lumaniare | 1 | 9 | 4 | 16 | 7 | 2 | 2 | 1 | 13 | 12 | 11 | 1 | 3 | 6 | 3 | 6 | 5 | 6 | 4 | 5 | 5 | 9 | 16 | 4 | 2 | 27 | 13 | 31
lumen per luminiare | 4000 | 4000 | 300 | 1200 | 1200 | 270 | 600 | 1000 | 4000 | 3600 | 21000 | 2000 | 4000 | 4,000 lumens | 400 lumens | 800 lumens | 4,000 lumens | 800 lumens | 2,000 lumens | 4,000 lumens | 800 lumens | 400 | 1800 lumens | 400 | 800 lumens | 7,000 lumens | 8,000 lumens | 7200 lumens
Luminaire type (LED) | Ceiling-mounted spot light | Flat Panel LED. | Recessed LED Downlight | LED Recessed Downlight. | LED Recessed Downlight. | LED Recessed Downlight | LED Recessed Downlight. | LED Utility Light | LED Recessed Panel | LED Panel Light | LED High Bay Light | LED Vapor Tight Fixture | LED Vapor Tight Fixture | LED Panel | LED Recessed Downlight | LED Recessed Downlight | LED Panel | LED Recessed Downlight | LED Panel | LED Panel | LED Recessed Downlight | flat panel LED | LED Recessed Downlight | recessed LED panel light | LED Recessed Downlight | LED Linear Strip | Vapor-Tight LED | LED Panel Light (2x4 ft)
Description (Model No) | Hue White and Color Ambiance Centris 4-Spot Ceiling Light | Lithonia CPX 2X4 4000LM 40K M2 | Energizer 4" LED Recessed Ceiling Light | Juno LED 6" Recessed Downlight | Juno LED 6" Recessed Downlight | Cree 4" LED Downlight | Halo RL560 Series LED | KT-WPLED10-840 | Lithonia Lighting CPX 2X2 | Philips CoreLine LED Panel 600x600 | Philips Ultra Efficient LED High Bay 150W | SHARK2-22N | SHARK2-48N | Philips CorePro LED Panel 40W | Philips CorePro LED Downlight 5W | Philips CorePro LED Downlight 10W | Philips CorePro LED Panel 40W | Philips CorePro LED Downlight 10W | Philips CorePro LED Panel 20W | Philips CorePro LED Panel 40W | Philips CorePro LED Downlight 10W | Lithonia CPX 2X4 4000LM 40K M2 | Philips CorePro LED Downlight 20W | Philips CoreLine LED Panel 600x600 36W 4000K | Philips CorePro LED Downlight 10W | Philips Ledalite TruGroove 4ft LED Strip | Philips Day-Brite Vapor-Tight LED (VT1) | Philips Ledalite TruGroove
mounting (Suspended Celling) | Ceiling-mounted | Recessed mounting | Recessed | Recessed ceiling installation. | Recessed ceiling installation. | Recessed Ceiling Mount | Recessed ceiling installation. | ceiling-mounted light | Recessed Ceiling Grid Mount | Surface Mount | Suspended | Ceiling or wall mount | Ceiling or wall mount | Ceiling Surface Mount (Recessed option available) | Recessed (Ceiling Mount) | Recessed (Ceiling Mount) | Ceiling Surface Mount (Recessed option available) | Recessed (Ceiling Mount) | Ceiling Surface Mount (Recessed option available) | Ceiling Surface Mount (Recessed option available) | Recessed (Ceiling Mount) | Recessed mounting | Recessed (Ceiling Mount) | Recessed | Recessed (Ceiling Mount) | Surface-mounted or suspended | Surface-mounted or suspended | Recessed, surface-mounted, or suspended
wattage(W) | 40 W | 40 | 6 | 12 | 12 | 3 | 9 | 10 | 40 | 36 | 150 | 24 | 48 | 40W | 5W | 10W | 40W | 10W | 20W | 40W | 10W | 40 | 20W | 36 | 10W | 55W | 65W | 56W
lumens( lm) | 4,600 lumens | 4000 | 300 | 1200 | 1200 | 270 | 600 | 1000 | 4000 | 3600 | 21000 | 2000 | 4000 | 4,000 lumens | 400 lumens | 800 lumens | 4,000 lumens | 800 lumens | 2,000 lumens | 4,000 lumens | 800 lumens | 4000 | 1800 lumens | 4000 | 800 lumens | 7,000 lm | 8,000 lm | 7200 lm
manufacturer | Philips Hue | Lithonia Lighting | Energizer | Juno Lighting | Juno Lighting | Cree | Halo | Keystone | Lithonia | Philips | Philips | RAB Lighting | RAB Lighting | Philips | Philips | Philips | Philips | Philips | Philips | Philips | Philips | Lithonia Lighting | Philips | Philips | Philips | Philips (Ledalite TruGroove Series) | Philips (Day-Brite) | Philips (Ledalite TruGroove Series)
Remarks | Provides both functional and ambient lighting, with individual spot adjustability |  |  | ENERGY STAR certified, dimmable. | ENERGY STAR certified, dimmable. | Energy-efficient, low-wattage | ENERGY STAR certified, smooth light distribution |  | Glare-free design, high efficiency | Slim, energy-efficient | Ideal for high ceilings and large spaces | IP66-rated for dust and water resistance. | IP66-rated for dust and water resistance. | Ideal for offices and workspaces, energy-efficient, uniform lighting | Suitable for small rooms, energy-efficient, compact | Suitable for minimalistic and serene settings, energy-efficient, long-lasting | Ideal for educational spaces, energy-efficient, uniform lighting | Ideal for low to medium height spaces, energy-efficient, long-lasting | Ideal for general spaces, provides even lighting, energy-efficient | Ideal for office spaces, energy-efficient, provides uniform lighting | Suitable for general illumination, energy-efficient, long-lasting |  | Suitable for general illumination in galleries, energy-efficient, long-lasting |  | Suitable for indoor spaces such as stairwells, energy-efficient, long-lasting | Glare-free, uniform illumination, ideal for electrical rooms | IP65-rated, dust & moisture resistant, ideal for mechanical rooms | Uniform illumination, glare-free, ideal for telecom environments
Driver | Integrated LED driver | constant current LED driver | Internal driver | Integrated driver | Integrated driver | Integrated LED driver | Integrated driver | internal constant-current LED driver. | Integrated Driver | LED Driver | high-efficiency driver | 0-10V | 0-10V | Integrated LED Driver | Integrated LED Driver | Integrated LED Driver | Integrated LED Driver | Integrated LED Driver | Integrated LED Driver | Integrated LED Driver | Integrated LED Driver | constant current LED driver | Integrated LED Driver | Integrated LED driver | Integrated LED Driver | Philips Advance Xitanium | Philips Advance Xitanium | Philips Advance Xitanium
CCT(K) | Adjustable from 2000K to 6500K | 4000 | 4000 | 4000 | 4000 | 4000 | 5000 | 4000 | 4000 | 3600 | 4000 | 4000 | 4000 | 4000K (Neutral White) | 3000K (Warm White) | 3000K (Warm White) | 4000K (Neutral White) | 4000K (Neutral White) | 4000K (Neutral White) | 4000K (Neutral White) | 3000K (Warm White) | 4000 | 4000K (Neutral White) | 4000 | 3000K (Warm White) | 4000K (Neutral White) | 4000K (Neutral White) | 5000K (Cool White)
CRI | 80 | 80 | >80 | >90 | >90 | > 80 | >90 | >80 | > 90 | 80+ | 80+ | >80 | >80 | ≥80 (Good color rendering) | ≥80 (Good color rendering) | ≥80 (Good color rendering) | ≥80 (Good color rendering) | ≥80 (Good color rendering) | ≥80 (Good color rendering) | ≥80 (Good color rendering) | ≥80 (Good color rendering) | 80 | ≥80 (Good color rendering) | 85 | ≥80 (Good color rendering for residential and commercial areas) | >80 | >80 | >80
Controls(V) | Philips Hue app, Bluetooth, Alexa, Google Assistant, Hue Bridge integration | 0-10 | 0-10 | Compatible with dimmers | Compatible with dimmers | Non-dimmable |  | Non-dimmable | 0-10 | Compatible with dimmers | Compatible with dimmers | Dimmable with compatible switch | Dimmable with compatible switch | Non-dimmable (Dimmable versions available) | Non-dimmable (Dimmable versions available) | Non-dimmable (Dimmable versions available) | Non-dimmable (Dimmable versions available) | Non-dimmable (dimmable versions available) | Non-dimmable (Dimmable versions available) | Non-dimmable (Dimmable versions available) | Non-dimmable (Dimmable versions available) | 0-10 | Non-dimmable (Dimmable versions available) | 0-10 | Non-dimmable (available dimmable versions) | 0-10V Dimmable, Motion & Daylight Sensor Compatible | 0-10V Dimmable, Motion & Daylight Sensor Compatible | 0-10V Dimmable, Motion & Daylight Sensor Compatible
voltage(V) | 24 V | 120 - 277 | 120 | 120V. | 120V. | 120 | 120V. | 120-277 | 120-277 | 120-277 | 120-277 | 120-277 | 120-277 | 120V | 120V | 120V | 120V | 120V | 120V | 120V | 120V | 120 - 277 | 120V | 120V - 277V | 120V | 120-277V AC | 120-277V AC | 120-277V AC
Efficacy(lm/W) | 115 lumens per watt (lm/W) | 100 | 50-60 | 100 | 100 | 90 | 66.7 | 100 | 105 | 100 | 140 | 83 | 83 | 100 lm/W | 80 lm/W | 80 lm/W | 100 lm/w | 80 lm/W | 100 lm/W | 100 lm/W | 80 lm/W | 100 | 90 lm/W | 110 | 80 lm/W | ~127 lumens per watt | ~123 lumens per watt | ~128 lumens per watt